## Info
© 2022 OJ Electronics A/S · ® The OJ trademark is a registered trademark belonging to OJ Electronics A/S
OJ-Air2Master
Modbus and BACnet protocol
Software version 6.54
Quick overview
The most common used parameters.
Modbus Info
General information about modbus RTU/TCP-IP
Modbus RTU Connection
How to connect Modbus RTU (RS-485)
BACnet Info
General information about BACnet TCP-IP
BACnet Connection
How to connect BACnet TCP-IP
Parameters
Complete list of all modbus and BACnet parameters.
15-09-2022

## Quick overview
BACnet/Modbus overview
Quick overview over the most used parameters
[5 empty] | BacNet | Modbus
|  |  |  | Actual exhaust temp. [1/100°C] | AI 22 | 3x0026
|  |  |  | Actual extract flow [l/s] | AI 7 | 3x0009
|  |  |  | Extract motor output percentage [1/100%] | AI 60 | 3x0083
|  |  |  | Setpoint for extract flow, low speed [l/s] | AV 12 | 4x0014
|  |  |  | Setpoint for extract flow, medium speed [l/s] | AV 254 | 4x0321
|  |  |  | Setpoint for extract flow, high speed [l/s] | AV 13 | 4x0015
|  |  |  | Rot. heat exchanger – output percent. [%] | AI 73 | 3x0097
|  |  |  | Actual outdoor temp. [1/100°C] | AI 20 | 3x0024
|  |  |  | Inlet filter pressure [Pa] | AI 27 | 3x0031
|  |  |  | Inlet filter monitor max. alarm limit [Pa] | AI 31 | 3x0039
|  |  |  | Extract filter pressure [Pa] | AI 28 | 3x0032
|  |  |  | Max. alarm limit, extract filter pressure drop [Pa] | AI 32 | 3x0040
|  |  |  | Actual inlet flow [l/s] | AI 5 | 3x0007
|  |  |  | Inlet motor output percentage [1/100%] | AI 51 | 3x0073
|  |  |  | Setpoint for inlet flow, low speed [l/s] | AV 10 | 4x0011
|  |  |  | Setpoint for inlet flow, medium speed [l/s] | AV 251 | 4x0320
|  |  |  | Setpoint for inlet flow, high speed [l/s] | AV 11 | 4x0012
|  |  |  | Actual room temperature [1/100 °C] | AI 21 | 3x0025
|  | BacNet | Modbus | Actual extract duct pressure [Pa] | AI 3 | 3x0005
| Actual operating mode | AI 0 | 3x0001 | Setpoint for duct pressure, extract, low speed [Pa] | AV 6 | 4x0007
| Operation ON/OFF | BI 0 | 1x0001 | Setpoint for duct pressure, extract, medium speed [Pa] | AV 255 | 4x0323
| Extended low speed –> Active | BI 3 | 1x0004 | Setpoint for duct pressure, extract, high speed [Pa] | AV 7 | 4x0008
| Extended high speed –> Active | BI 4 | 1x0005
| Alarm relay 1 (A-alarm) | BI 30 | 1x0035 | Actual inlet temperature [1/100°C] | AI 16 | 3x0020
| Alarm relay 2 (B-alarm) | BI 31 | 1x0036 | Control type setting | AV 133 | 4x0148
| Alarm reset signal (AutoReturn to zero) | BV 0 | 0x0001 | Temperature setpoint for actual control type | AV 134 | 4x0149
|  |  |  | Min. limit, inlet temp. [1/100°C] | AV 135 | 4x0150
|  |  |  | Max. limit, inlet temp. [1/100°C] | AV 136 | 4x0151
|  |  |  | Actual heating power [1/100%] | AI 36 | 3x0054
|  |  |  | Heating relay 1 | BI 26 | 1x0031
|  |  |  | Act. heating bat. temp.[1/100°C] | AI 26 | 3x0030
|  |  |  | Actual cooling power [1/100%] | AI 38 | 3x0056
|  |  |  | Actual inlet duct pressure [Pa] | AI 1 | 3x0003
| AI= Analog Input |  |  | Setpoint for duct pressure, inlet, low speed [Pa] | AV 2 | 4x0003
| AV= Analog Value |  |  | Setpoint for duct pressure, inlet, medium speed [Pa] | AV 252 | 4x0322
| BI= Binary Input |  |  | Setpoint for duct pressure, inlet, high speed [Pa] | AV 3 | 4x0004
BV= Binary Value
© 2022 OJ Electronics A/S · ® The OJ trademark is a registered trademark belonging to OJ Electronics A/S
15-09-2022

## Modbus info
Modbus RTU/TCP
OJ Air2, Program version 6.30 and later versions
Overview
This Protocol contains all Modbus addresses and registers in the OJ-Air2Master.
Updating of values in the individual registers is dependent on the actual configuration
of the air handling unit. It will, for example, be possible to read out water heating coil
temperature register 3x0030 irrespective of whether or not an water heating coil
is installed in the system concerned.
The value will, however, only be used if the associated temperature sensor is installed.
Modbus can access single addresses or several addresses simultaneously,
either reading or writing 1-bit or 16-bit values.
A Modbus address contains either a 1-bit value or a 16-bit integer.
Communication
TCP/IP: 1 x 10/100 Mbit Ethernet, RJ45 connector.
Modbus RS485: 1 x external Modbus, RS485, RJ12 connector, which can be set for 9.6 kBd, 19.2 kBd or 38.4 kBd.
Pin1 NC, Pin2 GND, Pin3 RS485 B, Pin4 RS485 A, Pin5 NC, Pin6 GND (see fig. 2).
Hand terminal: 1 x Modbus, RS485, 115 kBd, +24 V DC, RJ12 connector.
RS485 A: Not in use
RS485 B & C: 2 x shared local Modbus, RS485, 38.4 kBd, +24 V DC, RJ12 connector.
Standard Modbus TCP/IP kommunikationsport: 502
Modbus data format
Modbus data types are 1-bit values and 16-bit values.
Modbus Type |  | Description | Reference
Coil Status (R/W) |  | Discrete Output | 0x
Input Status (R) |  | Discrete Input | 1x
Holding Register (R/W) |  | 16-bit Output Register | 4x
Input register (R) |  | 16-bit Input Register | 3x
R = Read Only
R/W = Read / Write
Supported Modbus commands
OJ Air2 supports the following Modbus commands:
Function code | Description
1 | Read Coil Status
2 | Read Input Status
3 | Read Holding Registers
4 | Read Input Registers
5 | Force Single Coil
6 | Preset Single Registers
8 | Diagnostics. Sub-function 00 Only - Return Query Data (loop back)
15 | Force Multiple Coils
16 | Preset Multiple Registers
© 2022 OJ Electronics A/S · ® The OJ trademark is a registered trademark belonging to OJ Electronics A/S
15-09-2022

## Modbus Overview parameters (hidden)
Actual extract flow [l/s] |  |  | 3x0009
Extract motor output percentage [1/100%] |  |  | 3x0083 |  |  |  | Actual operating mode | 3x0001
Setpoint for extract flow, low speed [l/s] |  |  | 4x0014 |  |  |  | Operation ON/OFF | 1x0001
Setpoint for extract flow, high speed [l/s] |  |  | 4x0015 |  |  |  | Extended low speed –> Active | 1x0004
[7 empty] | Extended high speed –> Active | 1x0005
|  | Actual extract duct pressure [Pa] |  | 3x0005 |  |  | Alarm relay 1 (A-alarm) | 1x0035
|  | Setpoint for duct pressure, extract, low speed [Pa] |  | 4x0007 |  |  | Alarm relay 2 (B-alarm) | 1x0036
|  | Setpoint for duct pressure, extract, high speed [Pa] |  | 4x0008 |  |  | Alarm reset signal (AutoReturn to zero) | 0x0001
|  | Inlet filter pressure [Pa] |  | 3x0031
|  | Inlet filter monitor max. alarm limit [Pa] |  | 3x0039
[7 empty] | Actual inlet temperature [1/100°C] | 3x0020
[7 empty] | Control type setting | 4x0148
[7 empty] | Temperature setpoint for actual control type | 4x0149
[7 empty] | Extract filter pressure [Pa] | 3x0032
[7 empty] | Max. alarm limit, extract filter pressure drop [Pa] | 3x0040
[7 empty] | Actual room temperature [1/100 °C] | 3x0025
[7 empty] | Actual exhaust temp. [1/100°C] | 3x0026
[7 empty] | Min. limit, inlet temp. [1/100°C] | 4x0150
[7 empty] | Max. limit, inlet temp. [1/100°C] | 4x0151
[7 empty] | Actual inlet duct pressure [Pa] | 3x0003
[7 empty] | Setpoint for duct pressure, inlet, low speed [Pa] | 4x0003
[7 empty] | Setpoint for duct pressure, inlet, high speed [Pa] | 4x0004
[7 empty] | Actual inlet flow [l/s] | 3x0007
[7 empty] | Inlet motor output percentage [1/100%] | 3x0073
[7 empty] | Setpoint for inlet flow, low speed [l/s] | 4x0011
[7 empty] | Setpoint for inlet flow, high speed [l/s] | 4x0012
Actual outdoor temp. [1/100°C] 3x0024 |  |  |  |  | Actual heating power [1/100%] | 3x0054
[5 empty] | Heating relay 1 | 1x0031
| Rot. heat exchanger – output percent. [%] |  | 3x0092 |  | Act. heating bat. temp.[1/100°C] | 3x0030
|  |  | Actual cooling power [1/100%] |  | 3x0056
© 2016 OJ Electronics A/S · ® The Trade Mark OJ is an registered Trade Mark belonging to OJ Electronics A/S
06-07-16

## Modbus RTU Connection
© 2022 OJ Electronics A/S · ® The OJ trademark is a registered trademark belonging to OJ Electronics A/S
OJ Air2 Master Controller
RJ12 Modbus/RTU connection
Fig. 1 OJ Air Master, Connector diagram, visual topside down
Fig. 3 Modbus RS485 - RJ12 socket
Fig. 2 Configuration for communication via external Modbus
15-09-2022

## BacNet info
BACnet
OJ Air2, Program version 4.18 and subsequent versions.
Overview
BACnet features enable BACnet control and monitoring of a complete
Air Handling Unit (AHU), which is equipped with an OJ-Air2Master controller.
The BACnet functionality is implemented in OJ-Air2Masters with software version 2.00 or higher.
This protocol contains all BACnet addresses and registers in the OJ-Air2 Master. Updating of values in the individual registers is dependent on the actual configuration of the air handling unit. It will, for example, be possible to read out water heating coil temperature Analog Input Object Instance 26 irrespective of whether or not an water heating coil is installed in the system concerned. The value will, however, only be used if the associated temperature sensor is installed.
The OJ-Air2Master is a BACnet Advanced Application Controller (B-AAC)
Supported Data Link Layer Options: BACnet IP
Please also see the documents "OJ-Air2 BACnet PICS" (Protocol Implementation Conformance Statement)
and "OJ-Air2 EDE" (Engineering Data Exchange).
Communication
BACnet TCP/IP: 1 pcs. 10/100Mbit Ethernet, RJ45 socket
Standard BACnet TCP/IP communication port: 47808
Object Indentifier:
The Object_Identifier is automatic set to the last 5 digits in the OJ-Air2Master IP adress.
Samples: IP-adresse = 172.21.0.95 ………………..…….. Object Identifier = 95
IP-adresse = 155.37.0.216 ………………....... Object Identifier = 216
IP-adresse = 155.37.35.123 ………………..... Object Identifier = 35123
IP-adresse = 132.65.124.103 ……………….. Object Identifier = 24103
IP-adresse = 172.20.211.47 ………………..... Object Identifier = 11047
IP-adresse = 155.37.111.123 ………………... Object Identifier = 11123
IP-adresse = 168.25.111.1 ………………..….. Object Identifier = 11001
OBS! The Object_Identifier will only be set once and only when the OJ-Air2 Master is powered up or restarted
Max. 300 values ​​can at the same time be registered to the COV (Change Of Value)
BACnet Interoperability Building Blocks Supported
Data Sharing |  |  | DS-RP-B | Data Sharing-Read Property-B
Data sharing |  |  | DS-WP-B | Data Sharing-Write Property-B
Device Management |  |  | DM-DDB-B | Device Management-Dynamic Device Binding-B
Device Management |  |  | DM-DOB-B | Device Management-Dynamic Object Binding-B
Device Management |  |  | DM-DCC-B | Device Management-Dynamic Communication Control-B
Standard Object Types Supported
Object type |  | Properties
Analog Input |  | Object_Identifier, Object_Name, Object_Type, Present_Value, Status_Flags, Event_State, Out_Of_Service, Units, Min_Pres_Value, Max_Pres_Value, Resolution, Reliability, COV_Increment
Analog Value |  | Object_Identifier, Object_Name, Object_Type, Present_Value, Status_Flags, Event_State, Out_Of_Service, Units, Priority_Array, Relinquish_Default, COV_Increment.
Binary Input |  | Object_Identifier, Object_Name, Object_Type, Present_Value, Status_Flags, Event_State, Out_Of_Service, Polarity.
Binary Value |  | Object_Identifier, Object_Name, Object_Type, Present_Value, Status_Flags, Event_State, Out_Of_Service, Priority_Array, Relinquish_Default.
Device |  | Object_Identifier, Object_Name, Object_Type, System_Status, Vendor_Name, Vendor_Identifier, Model_Name, Firmware_Revision, Aplication_Software_Version, Location, Description, Protocol_Version, Protocol_Revision, Protocol_Services_Supported, Protocol_Object_Types_Supported, Object_list, Max_APDU_Length_Accepted, Segmentation_Supported, APDU_Timeout, Number_Of_APDU_Retries, Device_Address_Binding, Database_Revision.
© 2022 OJ Electronics A/S · ® The OJ trademark is a registered trademark belonging to OJ Electronics A/S
15-09-2022

## BacNet Connection
© 2022 OJ Electronics A/S · ® The OJ trademark is a registered trademark belonging to OJ Electronics A/S
Fig. 1 OJ Air Master, Connector diagram, visual topside down
OJ Air2 Master Controller
1 x RJ45 TCP/IP for BACnet/IP forbindelse for internal BACnet-server in OJ Air2 Master
15-09-2022

## Parameters
Intern ID | Component | Function | Standard/ Special | Name | SI Unit | Modbus register | SW vers. | BacNet parameter | SW vers. | Min | Max | Factory settings | Description | Dansk | English
| 1. Info | 1. Info | 1. Info | 1. Info |  | Coil status (R/W) |  | Binary value (R/W)
0x0E00 | AHU controller | Alarm | Standard | Alr_Reset |  | 0x0001 | x.xx | BV0 | x.xx | 0 | 1 |  | Alarm Reset-Signal (AutoReturn to zero) | Alarm Reset-Signal (AutoReturn til nul) | Alarm reset signal (AutoReturn to zero)
0x0002 | Heat exchanger | Cool recovery | Standard | CoolRecovFunc |  | 0x0002 | x.xx | BV1 | x.xx | 0 | 1 | 0 | CoolRecovery Function | Kølegenvinding ON/OFF | Cooling recovery: ON/OFF
0x0370 | AHU controller | Summer Night Cooling | Standard | SN_Func |  | 0x0003 | x.xx | BV2 | x.xx | 0 | 1 | 0 | Flag for SummerNight Function Set ON/OFF | Sommernat Køling; ON/OFF | Summer night cooling: ON/OFF
0x0380 | AHU controller | Summer/Winter comp. | Standard | SWTC_Func |  | 0x0004 | x.xx | BV3 | x.xx | 0 | 1 | 0 | Sum/Wint-TempComp Function ON/OFF | Sommer/Vinter Temp. Kompensering; ON/OFF | Summer/winter temp. compensation: ON/OFF
0x03C0 | Fan | Outdoor temp. comp. | Standard | FlwTmpCmpFunc |  | 0x0005 | x.xx | BV4 | x.xx | 0 | 1 | 0 | FlowOutTempCompensation Function ON/OFF | Flow-/Udetemperatur Kompensering; ON/OFF | Flow/outdoor temperature compensation: ON/OFF
0x03E0 | Damper, Recirculation | Recirculation heat | Standard | RecircFunc |  | 0x0006 | x.xx | BV5 | x.xx | 0 | 1 | 0 | Recirc Function ON/OFF | Recirkulation Funktion; ON/OFF | Recirculation: ON/OFF ("1" = Open damper)
0x0420 | Fan | Forced cooling | Standard | CoolFlwForceFc |  | 0x0007 | x.xx | BV6 | x.xx | 0 | 1 | 0 | Cool-FlowForce Function | Forceret flow ved kølebehov; ON/OFF | Forced flow with cooling demand: ON/OFF
0x0800 | AHU controller | Summer/winter time | Standard | TimeSw-SumFunc |  | 0x0008 | x.xx | BV7 | x.xx | 0 | 1 | 1 | Auto Summer/Winter Time Function | Automatisk Sommer-/Vinter Tid; ON/OFF | Automatic summer/winter time: ON/OFF
0x0810 | Fan | Speed | Standard | ExtDrfHiPeriod |  | 0x0009 | x.xx | BV8 | x.xx | 0 | 1 | 0 | Extended Periode = HI-Speed (High / Med OFF -> LO-Speed) | Forceret drift Høj (register 0x0010 skal være aktiv) Midlertidig overstyring af urdrift. | Input for forced high speed
0x0811 | Fan | Speed | Standard | ExtDrfPeriodON |  | 0x0010 | x.xx | BV9 | x.xx | 0 | 1 | 0 | Extended Periode Activated | Forceret drift Lav. Midlertidig overstyring af urdrift. | Run-on time for forced high speed active
0x0008 | Heat exchanger drive | Speed | Standard | EXC_CCV |  | 0x0011 | x.xx | BV26 | 6.41 | 0 | 1 | 0 | EXC-Rotation = CCV | Roterende varmeveksler, vend omdrejningsretning til mod uret (Counter Clock Wise) | Rotary heatexchanger, turn ratation direction to counter clock wise (CCW)
0x0812 | Fan | Speed | Standard | ExtDrfMePeriod |  | 0x0012 | x.xx | NA | NA | 0 | 1 | 0 | Extended Periode = Med-Speed (High / Med OFF -> LO-Speed) | Forceret drift Medium (register 0x0010 skal være aktiv) Midlertidig overstyring af urdrift. | Input for forced medium speed
| AHU controller | Summer Night Cooling | Standard | SN_FuncLoSpeed |  | 0x0013 | 6.41 | BV27 | 6.51 | 0 | 1 | 0 |  |  | Summer Night Cooling activated in low speed
| AHU controller | Speed | Standard | ExtHighSpdSet |  | 0x0014 | 6.51 | BV28 | 6.51 | 0 | 1 | 0 |  |  | External high speed start signal
0x0000 | Pressure | Calibration | Standard | ManZeroCali |  | 0x0020 | x.xx | BV10 | 4.18 | 0 | 1 | 0 | Start Manual ZeroCalibration (can bee used together wiht AutoZeroCalibration) Returns automatically back to zero (off) when calibration is completed | Start Manuel "0"-kalibrering (kan bruges samtidig med Automatisk "0"-kalibrering). Tilbagestilles automatisk til "0" (OFF), når kalibrering er afsluttet. | Start manual zero calibration (can be used together with automatic zero calibration) Is automatically reset to zero (OFF) once calibration has been completed
0x0001 | Pressure | Calibration | Standard | AutoZeroCali |  | 0x0021 | x.xx | BV11 | 4.18 | 0 | 1 | 0 | Auto ZeroCalibration Function | Automatisk "0"-kalibrering Funktion ON/OFF | Automatic zero calibration: ON/OFF
0x0390 | Filter | Alarm | Standard | FiltDynAlrFunc |  | 0x0022 | x.xx | BV12 | x.xx | 0 | 1 | 0 | Filter Dynamic Alarm function ON/OFF OFF -> Static AlarmLimit (Const) ON -> Dynamic AlarmLimit (Limit based on flow) | Filter Dynamisk Alarm funktion -> ON/OFF OFF -> Statisk Alarm Grænse (Konstant) ON -> Dynamisk Alarm Grænse (grænse på basis af flow) | Dynamic filter alarm –> ON/OFF OFF –> static alarm limit (constant) ON –> dynamic alarm limit (limit based on flow)
0x0391 | Filter | Calibration | Standard | FiltCalibrate |  | 0x0023 | x.xx | BV13 | x.xx | 0 | 1 | 0 | Start Filter Calibration. Returns automatically back to zero (off) when calibration is completed. ONLY FOR DYNAMIC-MODE | Start Filterkalibrering. Tilbagestilles automatisk til "0" (OFF), når kalibering er afsluttet. OBS! KUN NÅR INDSTILLET TIL “DYNAMIC-MODE” | Start filter calibration. Is automatically reset to zero (OFF) once calibration has been completed. NOTE! ONLY IF "DYNAMIC MODE" IS SET
0x0392 | Filter |  | Standard | FiltCaliDone |  | 0x0024 | x.xx | BV14 | 4.18 | 0 | 1 | 0 | Filter Calibration done (valid filterpress data) DYNAMICMODE ONLY | Filter Kalibrering udført (valide filter data) OBS! KUN NÅR INDSTILLET TIL “DYNAMIC-MODE” | Filter calibration completed (valid filter data) NOTE! ONLY IF "DYNAMIC MODE" IS SET
0x0436 | Combi coil | Control | Standard | CmbEnCtrlMB |  | 0x0025 | x.xx | BV21 | 6.20 | 0 | 1 | 0 | CombiCoil enable Heat/Cool ctrl via MB | Frigiv kombiflade til styring via ekstern Modbus | Enable combi coil for control via external Modbus [1=Modbus/0=Dig. input]
0x0437 | Combi coil | Control | Standard | CmbEnHeatMB |  | 0x0026 | x.xx | BV17 | x.xx | 0 | 1 | 1 | CombiCoil enable Heat via MB | Varmt vand til combiflade tilgængeligt | Hot water supply is available for the combi coil
0x0438 | Combi coil | Control | Standard | CmbEnCoolMB |  | 0x0027 | x.xx | BV18 | x.xx | 0 | 1 | 1 | CombiCoil enable Cool via MB | Koldt vand til combiflade tilgængeligt | Cold water supply is available for the combi coil
0x0095 | Temp. Out door | Control | Standard | MBTOutDAct |  | 0x0028 | x.xx | BV15 | x.xx | 0 | 1 | 0 | External Modbus OutdoorTemp active | Aktiver udetemperatur fra BMS | Activate outdoor temperature from BMS
0x0096 | Temp. Room | Control | Standard | MBTRoom1Activ |  | 0x0029 | x.xx | BV16 | x.xx | 0 | 1 | 0 | RoomModbus Temperature active | Aktiver rumtemperatur fra BMS | Activate room temperature from BMS
0x0410 | Damper, Recirculation | Recirculation heat | Standard | MBForceRecirc |  | 0x0030 | 4.18 | BV19 | 4.18 | 0 | 1 | 0 | Force recirc via Ext. Modbus | Overstyret omluft via Modbus | Force recirc via Ext. Modbus ("1" = Open damper)
0x0411 | Damper, Recirculation | Recirculation heat | Standard | MBEnblForceRec |  | 0x0031 | 4.18 | BV20 | 4.18 | 0 | 1 | 0 | Enable Modbus Force recirc signal | Tillad omluft til styring via ekstern Modbus | Enable Modbus Force recirc signal
| Filter | Alarm | Standard | FilOADynAlrFc |  | 0x0032 | 6.41 | BV22 | 6.41 | 0 | 1 | 0 |  |  | Filter (OA) Dynamic Alarm function ON/OFF OFF -> Static AlarmLimit (Const) ON -> Dynamic AlarmLimit (Limit based on flow)
| Filter | Alarm | Standard | FilSADynAlrFc |  | 0x0033 | 6.41 | BV23 | 6.41 | 0 | 1 | 0 |  |  | Filter (SA) Dynamic Alarm function ON/OFF OFF -> Static AlarmLimit (Const) ON -> Dynamic AlarmLimit (Limit based on flow)
| Filter | Alarm | Standard | FilEXDynAlrFc |  | 0x0034 | 6.41 | BV24 | 6.41 | 0 | 1 | 0 |  |  | Filter (EX) Dynamic Alarm function ON/OFF OFF -> Static AlarmLimit (Const) ON -> Dynamic AlarmLimit (Limit based on flow)
| Filter | Alarm | Standard | FilEX1DynAlrFc |  | 0x0035 | 6.41 | BV25 | 6.41 | 0 | 1 | 0 |  |  | Filter (EX1) Dynamic Alarm function ON/OFF OFF -> Static AlarmLimit (Const) ON -> Dynamic AlarmLimit (Limit based on flow)
| 1. Info | 1. Info | 1. Info | 1. Info |  | Input status (R) |  | Binary input (R) | 1. Info | 1. Info | 1. Info | 1. Info
0x1000 | AHU controller | Speed | Standard | Operation |  | 1x0001 | x.xx | BI0 | x.xx | 0 | 1 |  | Operation ON/OFF | Drift ON/OFF | Operation ON/OFF
0x1001 | AHU controller | Speed | Standard | ExtStop |  | 1x0002 | x.xx | BI1 | x.xx | 0 | 1 |  | External Stop | Ekstern stop | External stop
0x1002 | AHU controller | Speed | Standard | ExtHiSpeed |  | 1x0003 | x.xx | BI2 | x.xx | 0 | 1 |  | External HiSpeed | Ekstern høj hastighed | Externalhigh speed
0x1810 | AHU controller | Speed | Standard | ExtDrfLoSpeed |  | 1x0004 | x.xx | BI3 | x.xx | 0 | 1 |  | Extended LoSpeedDrift Active | Forlænget lav hastighed -> Aktiv | Extended low speed –> Active
0x1811 | AHU controller | Speed | Standard | ExtDrfHiSpeed |  | 1x0005 | x.xx | BI4 | x.xx | 0 | 1 |  | Extended HiSpeedDrift Active | Forlænget høj hastighed -> Aktiv | Extended high speed –> Active
0x1013 | AHU controller | Fire | Standard | ExtBrandStop |  | 1x0006 | x.xx | BI78 | x.xx | 0 | 1 |  | status Brandstop input | Ekstern brandstop indgang, status | Status Brandstop input
0x1812 | Fan | Speed | Standard | ExtDrfMeSpeed |  | 1x0007 | x.xx | BI225 | x.xx | 0 | 1 |  | Extended MediumSpeedDrift Active | Forlænget medium hastighed -> Aktiv | Extended medium speed –> Active
0x1341 | Heating coil, Electric | Status | Standard | ElBattPowerRed |  | 1x0010 | x.xx | BI5 | x.xx | 0 | 1 |  | EL-Coil Power Reduct (Lo Flow) | Energi til el-varmeflade reduceret p.g.a. lavt flow | Power to electric heating coil reduced due to low flow
0x1370 | AHU controller | Summer Night Cooling | Standard | SN_Drift |  | 1x0011 | x.xx | BI6 | x.xx | 0 | 1 |  | Flag for SummerNight er aktiv (run) | Sommernat køling er aktiv | Summer night cooling is active
0x1371 | AHU controller | Summer Night Cooling | Standard | SN_Reset |  | 1x0012 | x.xx | BI7 | x.xx | 0 | 1 |  | Flag for SummerNight Parm Reset (new start ready) | Reset parametre for sommer natkøling (Ny beregning startes) | Reset parameters for summer night cooling (new calculation is initiated)
0x1380 | AHU controller | Summer/Winter comp. | Standard | SWTC_WintComp |  | 1x0013 | x.xx | BI8 | x.xx | 0 | 1 |  | Winter-TempComp is active (status flag) | Vinter -temperatur kompensering er aktiv | Winter temperature compensation is active
0x1381 | AHU controller | Summer/Winter comp. | Standard | SWTC_SumComp |  | 1x0014 | x.xx | BI9 | x.xx | 0 | 1 |  | Summer-TempComp is active (status flag) | Sommer -temperatur kompensering er aktiv | Summer temperature compensation is active
0x13D0 | AHU controller | Summer/Winter comp. | Standard | SW_Status |  | 1x0015 | x.xx | BI10 | x.xx | 0 | 1 |  | Summer/Winter actual status (SW_Mode = 1..3): OFF - WinterMode ON - SummerMode | Sommer/Vinter aktuel status (SW_Mode = 1..3) OFF –> Vinter Drift ("0") ON – Sommer Drift ("1") | Summer/winter actual status OFF –> winter operation ("0") ON –> summer operation ("1")
0x13E1 | Damper, Recirculation | Recirculation heat | Standard | RecircStatus |  | 1x0016 | x.xx | BI11 | x.xx | 0 | 1 |  | Recirc Status | Recirkulation status | Recirculation status ("1" = Open damper)
0x100D | Heat exchanger | Speed | Standard | EXC_Exercise |  | 1x0017 | x.xx | BI12 | x.xx | 0 | 1 |  | EXC-Exercise Active | Motion af varmeveksler -> Aktiv | Exercising heat exchanger –> Active
0x1321 | Heat exchanger | Status | Standard | CExcIceProtect |  | 1x0018 | x.xx | BI13 | x.xx | 0 | 1 |  | Power for CrossEXC reduced because of ice protection | Signal til krydsveksler reduceret (frost beskyttelse) | Signal to cross-flow exchanger reduced (frost protection)
0x1103 | Fan | Status | Standard | SupDuctMinFlow |  | 1x0019 | x.xx | BI14 | x.xx | 0 | 1 |  | Supply DuctPressRegulator Run at MinFlow | tilluft kanal tryk-regulator regulereret til Min. Flow | Supply duct pressure controller reduced to min. flow
0x1104 | Fan | Status | Standard | SupDuctMaxFlow |  | 1x0020 | x.xx | BI15 | x.xx | 0 | 1 |  | Supply DuctPressRegulator Run at MaxFlow | tilluft kanal tryk-regulator regulereret til Max. Flow | Supply duct pressure controller increased to max. flow
0x1203 | Fan | Status | Standard | ExtDuctMinFlow |  | 1x0021 | x.xx | BI16 | x.xx | 0 | 1 |  | Extract DuctPressRegulator Run at MinFlow | fraluft kanal tryk-regulator regulereret til Min. Flow | Extract duct pressure controller reduced to min. flow
0x1204 | Fan | Status | Standard | ExtDuctMaxFlow |  | 1x0022 | x.xx | BI17 | x.xx | 0 | 1 |  | Extract DuctPressRegulator Run at MaxFlow | fraluft kanal tryk-regulator regulereret til Max. Flow | Extract duct pressure controller increased to max. flow
0x1003 | Heat exchanger | Status | Standard | CoolRecovery |  | 1x0023 | x.xx | BI18 | x.xx | 0 | 1 |  | CoolRecovery Status | Kølegenvinding -> Status | Cooling recovery –> status
0x1332 | Heating coil 1, Water | Status | Standard | HW1FrostReg |  | 1x0024 | x.xx | BI19 | x.xx | 0 | 1 |  | HeatWaterTemp -FrostReg Active | Cirkulationspumpe på varmeflade; Frost Regulering -> Aktiv | Circulation pump on heating coil: Frost protection –> Active
0x1333 | Heating coil 1, Water | Status | Standard | HW1PumpExer |  | 1x0025 | x.xx | BI20 | x.xx | 0 | 1 |  | HeatWater PumpExercise active | Cirkulationspumpe på varmeflade; Pumpemotion -> Aktiv | Circulation pump on heating coil: Pump exercising –> Active
0x1350 | Cooling coil | Status | Standard | CW_PumpExer |  | 1x0026 | 4.18 | BI21 | 4.18 |  |  |  | CoolWaterCoil PumpExercise active | Cirkulationspumpe på køleflade; Pumpemotion -> Aktiv | CoolWaterCoil PumpExercise active
0x1402 | Heating coil 1, Electric | Status | Standard | Heat_FlwDnReg |  | 1x0027 | x.xx | BI22 | x.xx | 0 | 1 |  | FlowDownReg Active | Signal til varmeflade reduceret (for lavt flow) -> Aktiv | Signal to heating coil reduced (insufficient flow) –> Active
0x1460 | AHU controller | Status | Standard | TempRegMinSup |  | 1x0028 | x.xx | BI23 | x.xx | 0 | 1 |  | Is set when Min SupplyTempReg is active. Only used for TempRegMode 1 and 2 (RoomReg) | “1” når min. tilluftstemperatur regulering er aktiv. Kun aktivt når “TempRegMode” er 1 eller 2 (Rum-regulering) | "1" when min. supply temperature control is active. Only active when TempRegMode is 1 or 2 (room temp. control)
0x1461 | AHU controller | Status | Standard | TempRegMaxSup |  | 1x0029 | x.xx | BI24 | x.xx | 0 | 1 |  | Is set when Max SupplyTempReg is active.Only used for TempRegMode 1 and 2 (RoomReg) | “1” når max. tilluftstemperatur Regulering er aktiv. Kun aktivt når “TempRegMode” er 1 eller 2 (Rum-regulering) | "1" when max. supply temperature control is active. Only active when TempRegMode is 1 or 2 (room temp. control)
0x1922 | Heat exchanger | Status | Standard | BattEXC_Exer |  | 1x0030 | x.xx | BI25 | x.xx | 0 | 1 |  | WaterCoil EXC PumpExercise active | Cirkulationspumpe på Varme genvingsflade; Pumpemotion -> Aktiv | Circulation pump on heat recovery coil: Pump exercising –> Active
0x1400 | Heating coil 1 | Status | Standard | Heat_RE1 |  | 1x0031 | x.xx | BI26 | x.xx | 0 | 1 |  | Heat Relay 1 | Varme Relæ 1 | Heating relay 1
0x1420 | Cooling coil | Status | Standard | Cool_RE1 |  | 1x0032 | x.xx | BI27 | x.xx | 0 | 1 |  | Cool Relay 1 | Køle Relæ 1 | Cooling relay 1
0x1921 | Heat exchanger | Status | Standard | BattEXC_PumpRE |  | 1x0033 | x.xx | BI28 | x.xx | 0 | 1 |  | WaterCoil EXC PumpRelay | Cirkulationspumpe på varme genvingsflade; Pumpe -> Kører | Circulation pump on heat recovery coil: Pump –> Running
0x100E | AHU controller | Alarm | Standard | AlrActive |  | 1x0034 | x.xx | BI29 | x.xx | 0 | 1 |  | Least one Active Alarm | Mindst én aktiv alarm | At least one active alarm
0x1480 | AHU controller | Alarm | Standard | Alr_RE1 |  | 1x0035 | x.xx | BI30 | x.xx | 0 | 1 |  | AlarmRelay-1 (A-Alarm) | alarmRelæ-1 (A-alarm) | Alarm relay 1 (A-alarm)
0x1481 | AHU controller | Alarm | Standard | Alr_RE2 |  | 1x0036 | x.xx | BI31 | x.xx | 0 | 1 |  | AlarmRelay-2 (B-Alarm) | alarmRelæ-2 (B-alarm) | Alarm relay 2 (B-alarm)
0x1488 | AHU controller | Fire | Standard | Alr_FireSignal |  | 1x0037 | x.xx | BI32 | x.xx | 0 | 1 |  | FireAlarm-Signal (sensor in room) | Brand alarm-signal (Rumføler) | Fire alarm signal (room sensor)
0x1489 | AHU controller | Smoke | Standard | Alr_SmokeSig |  | 1x0038 | x.xx | BI33 | x.xx | 0 | 1 |  | SmokeAlarm-Signal (sensor in duct) | Røg / Brand alarm-Signal (Føler i kanal) | Smoke/fire alarm signal (duct sensor)
0x1485 | Heating coil, Electric | Alarm | Standard | EL1_OverHtBac |  | 1x0039 | x.xx | BI219 | x.xx | 0 | 1 |  | ElCoil1 Overheat State to Bacnet | EL-varmeflade; Høj temperatur alarm signal | Electric coil: High temperature alarm signal
0x1E3D | Heating coil, Electric | Alarm | Standard | AlrElBattCont |  | 1x0040 | x.xx | BI220 | x.xx | 0 | 1 |  | EL-Coil Contactor Error (Contact hang) | EL-varmeflade; Relæ hænger | Electric coil: Relay stuck
0x1390 | Filter | Alarm | Standard | FiltSupAlarm |  | 1x0041 | x.xx | BI35 | x.xx | 0 | 1 |  | Filter Alarm for Sup-Filter (pressure above Limit) | Filter alarm for tillufts-Filter (Trykfald over indstillet Grænse) | Filter alarm for supply filter (pressure drop above set limit)
0x1391 | Filter | Alarm | Standard | FiltExtAlarm |  | 1x0042 | x.xx | BI36 | x.xx | 0 | 1 |  | Filter Alarm for Ext-Filter (pressure above Limit) | Filter alarm for fralufts-Filter (Trykfald over indstillet Grænse) | Filter alarm for extract filter (pressure drop above set limit)
0x1322 | Heat exchanger | Status | Special | CExcDeIcing |  | 1x0043 | x.xx | BI297 | 6.51 | 0 | 1 |  | Power for CrossEXC reduced as a deicing procedure has started | Reducering af krydsveksler p.g.a. afisning; afisning startet | Reduction of cross-flow exchanger due to de-icing; deicing started
0x13B1 | Heating coil 2, Electric | Status | Standard | ElBat2PowerRed |  | 1x0045 | x.xx | BI298 | 6.51 | 0 | 1 |  | EL-Coil2 Power Reduct (Lo Flow) | EL-flade 2 Effekt Reduktion aktiv p.g.a. lavt flow | Electric coil 2 - Output reduction active due to low flow
0x1394 | Filter | Alarm | Standard | FiltSup2Alarm |  | 1x0048 | 4.18 | BI253 | 4.18 | 0 | 1 |  | Filter Alarm for Sup2-Filter (pressure above Limit) | Filter Alarm for Tilluft2-Filter (trykfald over alarmgrænse) | Filter Alarm for Sup2-Filter (pressure above Limit)
0x1395 | Filter | Alarm | Standard | FiltExt2Alarm |  | 1x0049 | 4.18 | BI254 | 4.18 | 0 | 1 |  | Filter Alarm for Ext2-Filter (pressure above Limit) | Filter Alarm for Fraluft2-Filter (trykfald over alarmgrænse) | Filter Alarm for Ext2-Filter (pressure above Limit)
0x1100 | Temp. Supply | Alarm | Standard | SupTempSensErr |  | 1x0050 | x.xx | BI37 | x.xx | 0 | 1 |  | SupplyTempSensor -Error | Tillufts temparatur føler – Følerfejl | Supply temperature sensor – sensor fault
0x1200 | Temp. Extract | Alarm | Standard | ExtTempSensErr |  | 1x0051 | x.xx | BI38 | x.xx | 0 | 1 |  | ExtractTempSensor -Error | Fralufts temparatur føler – Følerfejl | Extract temperature sensor – sensor fault
0x1300 | Temp. Out door | Alarm | Standard | OutDoorSensErr |  | 1x0052 | x.xx | BI39 | x.xx | 0 | 1 |  | OutDoorTemp -Sensor Error | Ude temparatur føler – Følerfejl | Outdoor temperature sensor – sensor fault
0x1310 | Temp. Room | Alarm | Standard | RoomSensErr |  | 1x0053 | x.xx | BI40 | x.xx | 0 | 1 |  | RoomTemp -Sensor Error | Rum temparatur føler – Følerfejl | Room temperature sensor – sensor fault
0x1320 | Temp. Exhaust | Alarm | Standard | ExhaustSensErr |  | 1x0054 | x.xx | BI41 | x.xx | 0 | 1 |  | ExhaustTemp -Sensor Error | Afkast temparatur føler – Følerfejl | Exhaust temperature sensor – sensor fault
0x1330 | Heating coil 1, Water | Alarm | Standard | HW1SensErr |  | 1x0055 | x.xx | BI42 | x.xx | 0 | 1 |  | HeatWaterTemp -Sensor Error | Varmeflade temparatur føler – Følerfejl | Heating coil temperature sensor – sensor fault
0x1920 | Heat exchanger | Alarm | Standard | BattEXC_SensEr |  | 1x0056 | x.xx | BI43 | x.xx | 0 | 1 |  | WaterCoil EXC Temp -Sensor Error | Varmegenvindings flade temperatur føler – Følerfejl | Heat recovery coil temperature sensor – sensor fault
0x1331 | Heating coil 1, Water | Alarm | Standard | HW1FrostAlr |  | 1x0057 | x.xx | BI44 | x.xx | 0 | 1 |  | HeatWaterTemp -FrostReg Alarm | Varmeflade –Frost alarm | Heating coil frost alarm
0x1428 | Cooling coil | Alarm | Standard | Cool_SumAlarm |  | 1x0060 | x.xx | BI45 | x.xx | 0 | 1 |  | Cool SumAlarmFlag | Køling fælles alarm | Cooling shared alarm
0x1429 | Cooling coil | Alarm | Standard | Cool_DI1_Alarm |  | 1x0061 | x.xx | BI46 | x.xx | 0 | 1 |  | Cool Digital Alarm-1 Input | Køling digital alarm-1 Indgang | Cooling digital alarm 1 input
0x142A | Cooling coil | Alarm | Standard | Cool_DI2_Alarm |  | 1x0062 | x.xx | BI47 | x.xx | 0 | 1 |  | Cool Digital Alarm-2 Input | Køling digital alarm-2 Indgang | Cooling digital alarm 2 input
0x142B | Cooling coil | Alarm | Standard | Cool_DI3_Alarm |  | 1x0063 | x.xx | BI48 | x.xx | 0 | 1 |  | Cool Digital Alarm-3 Input | Køling digital alarm-3 Indgang | Cooling digital alarm 3 input
0x142C | Cooling coil | Alarm | Standard | Cool_DI4_Alarm |  | 1x0064 | x.xx | BI49 | x.xx | 0 | 1 |  | Cool Digital Alarm-4 Input | Køling digital alarm-4 Indgang | Cooling digital alarm 4 input
0x1101 | Fan, Supply drive | Status | Standard | SupMotorON |  | 1x0070 | x.xx | BI50 | x.xx | 0 | 1 |  | SupplyMotor ON/OFF | Tillufts ON/OFF | Supply motor ON/OFF
0x1102 | Fan, Supply drive | Alarm | Standard | SupMotorAlarm |  | 1x0071 | 4.18 | BI51 | 4.18 | 0 | 1 |  | SupplyMotor Alarm | Tillufts tilluftsmotor | Supply Motor Alarm
0x1A40 | Fan, Supply drive | Alarm | Standard | FCsupMtrAlrVlo |  | 1x0072 | x.xx | BI52 | x.xx | 0 | 1 |  | SupplyMotor Vlo Alarm | Tillufts spænding lav alarm (kun ved OJ-FC) | Supply motor low voltage alarm (only with OJ-FC)
0x1A41 | Fan, Supply drive | Alarm | Standard | FCsupMtrAlrVhi |  | 1x0073 | x.xx | BI53 | x.xx | 0 | 1 |  | SupplyMotor Vhi Alarm | Tillufts høj spændingsgrænse alarm (kun ved OJ-FC) | Supply motor high voltage alarm(only with OJ-FC)
0x1A42 | Fan, Supply drive | Alarm | Standard | FCsupMtrAlrIhi |  | 1x0074 | x.xx | BI54 | x.xx | 0 | 1 |  | SupplyMotor Ihi Alarm | Tillufts høj strøm alarm (kun ved OJ-FC), motorbeskyttelse | Supply motor high current alarm (only with OJ-FC), motor protection
0x1A43 | Fan, Supply drive | Alarm | Standard | FCsupMtrAlrTmp |  | 1x0075 | x.xx | BI55 | x.xx | 0 | 1 |  | SupplyMotor Temp Alarm | Tillufts temperatur alarm (kun ved OJ-FC) | Supply motor temperature alarm (only with OJ-FC)
0x1A44 | Fan, Supply drive | Alarm | Standard | FCsupMtrAlrPhs |  | 1x0076 | x.xx | BI56 | x.xx | 0 | 1 |  | SupplyMotor Phase Alarm | Tillufts fasefejl alarm (kun ved OJ-FC) | Supply motor phase fault alarm (only with OJ-FC)
0x1EB8 | Fan, Supply drive | Alarm | Standard | FCAlrSupOldRip |  | 1x0077 | x.xx | BI299 | 6.51 | 0 | 1 |  | Ripplealarm from old FC Supply | Tillufts Ripple-spænding alarm (kun ved OJ-FC) | Supply motor ripple voltage alarm (only with OJ-FC)
0x1A46 | Fan, Supply drive | Alarm | Standard | FCsupMtrIhiLim |  | 1x0078 | x.xx | BI58 | x.xx | 0 | 1 |  | SupplyMotor I Hi Limit | Tillufts høj strøm Grænse; kortslutningsbeskyttelse (kun ved OJ-FC) | Supply motor high current limit: short-circuit protection (only with OJ-FC)
0x1A45 | Fan, Supply drive | Alarm | Standard | FCsupMtrAlrRip |  | 1x0079 | 4.18 | BI57 | 4.18 | 0 | 1 |  | SupplyMotor V Ripple Alarm | Tilluftsmotor - V Ripple alarm | SupplyMotor V Ripple Alarm
0x1201 | Fan, Extract drive | Status | Standard | ExtMotorON |  | 1x0080 | x.xx | BI59 | x.xx | 0 | 1 |  | ExtractMotor ON/OFF | Fraluftsmotor ON/OFF (kun OJ-FC) | Extract motor ON/OFF (only with OJ-FC)
0x1A60 | Fan, Extract drive | Alarm | Standard | FCextMtrAlrVlo |  | 1x0082 | x.xx | BI61 | x.xx | 0 | 1 |  | ExtractMotor Vlo Alarm | Fraluftsmotor alarm for lav spænding (kun ved OJ-FC) | Extract motor low voltage alarm (only with OJ-FC)
0x1A61 | Fan, Extract drive | Alarm | Standard | FCextMtrAlrVhi |  | 1x0083 | x.xx | BI62 | x.xx | 0 | 1 |  | ExtractMotor Vhi Alarm | Fraluftsmotor høj spændingsgrænse alarm (kun ved OJ-FC) | Extract motor high voltage alarm (only with OJ-FC)
0x1A62 | Fan, Extract drive | Alarm | Standard | FCextMtrAlrIhi |  | 1x0084 | x.xx | BI63 | x.xx | 0 | 1 |  | ExtractMotor Ihi Alarm | Fraluftsmotor høj strømgrænse alarm (kun ved OJ-FC) | Extract motor high current alarm (only with OJ-FC)
0x1A63 | Fan, Extract drive | Alarm | Standard | FCextMtrAlrTmp |  | 1x0085 | x.xx | BI64 | x.xx | 0 | 1 |  | ExtractMotor Temp Alarm | Fraluftsmotor temperatur alarm (kun ved OJ-FC) | Extract motor temperature alarm (only with OJ-FC)
0x1A64 | Fan, Extract drive | Alarm | Standard | FCextMtrAlrPhs |  | 1x0086 | x.xx | BI65 | x.xx | 0 | 1 |  | ExtractMotor Phase Alarm | Fraluftsmotor alarm for fasefejl (kun ved OJ-FC) | Extract motor phase fault alarm (only with OJ-FC)
0x1EB9 | Fan, Extract drive | Alarm | Standard | FCAlrExtOldRip |  | 1x0087 | x.xx | BI300 | 6.51 | 0 | 1 |  | Ripplealarm from old FC Extract | Fraluftsmotor Ripple-spænding alarm (kun ved OJ-FC) | Extract motor ripple voltage alarm (only with OJ-FC)
0x1A66 | Fan, Extract drive | Alarm | Standard | FCextMtrIhiLim |  | 1x0088 | x.xx | BI67 | x.xx | 0 | 1 |  | ExtractMotor I Hi Limit | Fraluftsmotor høj strømgrænse (kun ved OJ-FC) | Extract motor high current limit (only with OJ-FC)
0x1A65 | Fan, Extract drive | Alarm | Standard | FCextMtrAlrRip |  | 1x0089 | 4.18 | BI66 | 4.18 | 0 | 1 |  | ExtractMotor V Ripple Alarm | Fraluftsmotor - V Ripple alarm | ExtractMotor V Ripple Alarm
0x1A70 | Heat exchanger drive | Status | Standard | EXC_ON |  | 1x0090 | x.xx | BI68 | x.xx | 0 | 1 |  | EXC-MotorCtrl ON/OFF | Roterende varmeveksler - Motorregulering ON/OFF (kun ved OJ-RHX2M) | Rotary heat exchanger – motor control ON/OFF (only with OJ-RHX2M)
0x1A71 | Heat exchanger drive | Status | Standard | EXC_Reset |  | 1x0091 | x.xx | BI69 | x.xx | 0 | 1 |  | EXC-Reset Signal | Roterende varmeveksler - Reset signal (kun ved OJ-RHX2M) | Rotary heat exchanger – reset signal (only with OJ-RHX2M)
0x1A73 | Heat exchanger drive | Status | Standard | EXC_Direction |  | 1x0092 | x.xx | BI70 | x.xx | 0 | 1 |  | EXC-Rotation Direction | Roterende varmeveksler - Omdrejningsretning (kun ved OJ-RHX2M) | Rotary heat exchanger – rotation direction (only with OJ-RHX2M)
0x1A80 | Heat exchanger drive | Alarm | Standard | EXC_RotAlarm |  | 1x0093 | x.xx | BI71 | x.xx | 0 | 1 |  | EXC-Rotation Alarm | Roterende varmeveksler - Rotation alarm (kun ved OJ-RHX2M) | Rotary heat exchanger – rotation alarm (only with OJ-RHX2M)
0x1A81 | Heat exchanger drive | Alarm | Standard | EXC_VloAlarm |  | 1x0094 | x.xx | BI72 | x.xx | 0 | 1 |  | EXC-Lo Voltage Alarm | Roterende varmeveksler alarm for underspænding (kun ved OJ-RHX2M) | Rotary heat exchanger – low voltage alarm (only with OJ-RHX2M)
0x1A82 | Heat exchanger drive | Alarm | Standard | EXC_VhiAlarm |  | 1x0095 | x.xx | BI73 | x.xx | 0 | 1 |  | EXC-Hi Voltage Alarm | Roterende varmeveksler alarm for overspænding (kun ved OJ-RHX2M) | Rotary heat exchanger – high voltage alarm (only with OJ-RHX2M)
0x1A83 | Heat exchanger drive | Alarm | Standard | EXC_IhiAlarm |  | 1x0096 | x.xx | BI74 | x.xx | 0 | 1 |  | EXC-Hi Current Alarm | Roterende varmeveksler alarm for høj strøm (kun ved OJ-RHX2M) | Rotary heat exchanger – high current alarm (only with OJ-RHX2M)
0x1A84 | Heat exchanger drive | Alarm | Standard | EXC_TempAlarm |  | 1x0097 | x.xx | BI75 | x.xx | 0 | 1 |  | EXC-Temperature Alarm | Roterende varmeveksler - Temperatur alarm (kun ved OJ-RHX2M) | Rotary heat exchanger – temperature alarm (only with OJ-RHX2M)
0x1A88 | Heat exchanger drive | Status | Standard | EXC_RotSignal |  | 1x0098 | x.xx | BI76 | x.xx | 0 | 1 |  | EXC-HallSensor Signal | Roterende varmeveksler - Rotation signal (kun ved OJ-RHX2M) | Rotary heat exchanger – rotation signal (only with OJ-RHX2M)
0x1A89 | Heat exchanger drive | Alarm | Standard | EXC_Overload |  | 1x0099 | x.xx | BI77 | x.xx | 0 | 1 |  | EXC-Moment Overload | Roterende varmeveksler - Moment overbelastning (kun ved OJ-RHX2M) | Rotary heat exchanger – torque overload (only with OJ-RHX2M)
0x1298 | Preheater coil, electric | Status | Standard | PH_PowReduce |  | 1x0100 | x.xx | BI93 | x.xx | 0 | 1 |  | Power reduce, airflow | Forvarmeflade - Effektreduktion, lav luftmængde | Pre-heating coil - Output reduction, low air volume
0x1292 | Preheater coil, water | Status | Standard | PHFrostRegAct |  | 1x0101 | x.xx | BI89 | x.xx | 0 | 1 |  | Frost regulation active | Forvarmeflade - Frost regulering aktiv | Pre-heating coil - Relay for active heating/cooling
0x1294 | Preheater coil | Status | Standard | PHHeatRelay |  | 1x0102 | x.xx | BI91 | x.xx | 0 | 1 |  | Relay Heat / Cool | Forvarmeflade - Relæ for aktiv varme/køle | Pre-heating coil - Frost protection active
0x1295 | Preheater coil, water | Alarm | Standard | PHFrzAlrCool |  | 1x0103 | x.xx | BI301 | 6.51 | 0 | 1 |  | Frost Alarm Cooling | Forvarmeflade - Frost Alarm Køling | Pre-heating coil - Frost alarm, cooling
0x1297 | Preheater coil, electric | Alarm | Standard | PH_Overheat |  | 1x0104 | x.xx | BI92 | x.xx | 0 | 1 |  | Overheat error | Forvarmeflade -Overhedning fejl | Pre-heating coil - Overheating fault
0x129A | Preheater coil, water | Alarm | Standard | PH_HWBSensErr |  | 1x0105 | x.xx | BI94 | x.xx | 0 | 1 |  | Returnwater sensor error | Forvarmeflade - Returføler; følerfejl | Pre-heating coil - Return sensor - Sensor fault
0x1291 | Preheater coil, water | Alarm | Standard | PHFreezeAlarm |  | 1x0106 | x.xx | BI88 | x.xx | 0 | 1 |  | Frost alarm | Forvarmeflade - Frost alarm | Pre-heating coil - Frost alarm
0x129C | Preheater coil | Status | Standard | PHHeatRelay2 |  | 1x0107 | x.xx | BI226 | x.xx | 0 | 1 |  | Relay 2 Heat / Cool | Forvarmeflade - Varmerelæ 2 | Preheater - heat relay 2
0x129D | Preheater coil | Status | Special | PHHeatRelay3 |  | 1x0108 | x.xx | BI176 | x.xx | 0 | 1 |  | Relay 3 Heat / Cool | Forvarmeflade - Varmerelæ 3 (Varme/Køl) | Pre-heating coil - Heat relay 3 (Heat/Cool)
0x1293 | Preheater coil, water | Status | Standard | PHPumpExer |  | 1x0109 | 4.18 | BI90 | 4.18 | 0 | 1 |  | Pre-heater Pump exercise active | Forvarmeflade - Pumpemotion aktiv | Pre-heater Pump exercise active
0x13F0 | Heat pump | Status | Special | HP_CoolingActv |  | 1x0110 | x.xx | BI108 | x.xx | 0 | 1 |  | Signal for the 4-way-valve in HeatPump, to allow for either cooling or heating: 0-Heating, 1-Cooling | Relæudgang changeover ventil (varme/køl) for varmepumpe. | Changeover relay heatpump active
0x13F2 | Heat pump | Status | Special | HP_De-icingAct |  | 1x0111 | x.xx | BI109 | x.xx | 0 | 1 |  | Heatpump is beeing de-iced flag | Status bit for afisning af varmepumpe | Status bit: De-icing of heatpump
0x1122 | Cooling coil | Status | Special | NO_CStopRTStat |  | 1x0112 | x.xx | BI107 | x.xx | 0 | 1 |  | RoomTemp cool stop active | Kølestop via rumtemperatur | Cooling stopped by room temperature
0x1123 | Cooling coil | Status | Special | NO_CRecovStat |  | 1x0113 | x.xx | BI106 | x.xx | 0 | 1 |  | Coolrecovery over damper active | Kølegenving via spjæld aktiv | Coolrecovery over damper active ("1" = Open damper)
0x1EA0 | Heat exchanger | Alarm | Special | AlrNoREXCali |  | 1x0114 | x.xx | BI104 | x.xx | 0 | 1 |  | Rot.EXC Pressure not calibrated | Alarm for ikke kalibreret tryktransmitter (rotor tilisnings vagt) | Alarm - pressure transmitter not calibrated (Ice guard rotor heat exchanger)
0x1EA1 | Heat exchanger | Alarm | Special | AlrSensREXNC |  | 1x0115 | x.xx | BI105 | x.xx | 0 | 1 |  | Rot.EXC PressureSensor not configurated | Alarm for ikke konfigereret tryktransmitter (rotor tilisnings vagt) | Alarm - pressure transmitter not configered (Ice guard rotor heat exchanger)
0x1EA2 | Heat exchanger | Alarm | Special | AlrRexFrozen |  | 1x0116 | x.xx | BI110 | x.xx | 0 | 1 |  | Rot.EXC frozen, high pressure | Roterende varmeveksler tiliset - højt tryk over veksler | Alarm - rotor heat exchanger blocked by ice (high pressure over rotor wheel)
0x1EA3 | Heat exchanger | Alarm | Special | AlrRexDusty |  | 1x0117 | x.xx | BI111 | x.xx | 0 | 1 |  | Rot.EXC dusty, high pressure | Roterende varmeveksler tilsmudset - højt tryk over veksler | Alarm - rotor heat exchanger blocked by dirt (high pressure over rotor wheel)
0x1E97 | Heat exchanger | Alarm | Standard | AlrEXCEffToLow |  | 1x0118 | 4.18 | BI95 | 4.18 | 0 | 1 |  | Heat recovery efficiency below alarm limit | Virkningsgrad for varmegenvindingen er under alarmgrænse | Alarm - Heat recovery efficiency below alarm limit
| Damper, Fire | Alarm | Standard | AlrFireDmpNCls |  | NA | NA | BI308 | 6.51 | 0 | 1 |  | Alarm, Fire damper not closed | Alarm, Brandspjæld ikke lukket i forbindelse med test | Alarm, Fire damper not closed
| Damper, Fire | Alarm | Standard | AlrFireDmpNOpn |  | NA | NA | BI309 | 6.51 | 0 | 1 |  | Alarm, Fire damper not open | Alarm, Brandspjæld ikke åbnet i forbindelse med test | Alarm, Fire damper not open
| Damper, Fire | Status | Standard | FireDmpTstActv |  | NA | NA | BI310 | 6.51 | 0 | 1 |  |  |  | Fire damper test is ongoing
| Fan Supply Backup | Alarm | Standard | SupBMotorAlarm |  | 1x0119 | 6.51 | BI295 | 6.51 | 0 | 1 |  |  |  | Supply Backup Motor Alarm
| Fan Exhaust Backup | Alarm | Standard | ExhBMotorAlarm |  | 1x0120 | 6.51 | BI296 | 6.51 | 0 | 1 |  |  |  | Exhaust Backup Motor Alarm
| Heat pump | Status | Special | HP_TSExtAirErr |  | 1x0121 | 6.51 | BI311 | 6.51 | 0 | 1 |  |  |  | Temperature sensor extract air after HeatPump - Sensor fault
| Motor Supply Backup | Alarm | Standard | AlrSupBMtr |  | 1x0329 | 6.51 | BI292 | 6.51 | 0 | 1 |  |  |  | SupBackupMotor Alarm
| Motor Exhaust Backup | Alarm | Standard | AlrExhBMtr |  | 1x0330 | 6.51 | BI293 | 6.51 | 0 | 1 |  |  |  | ExhBackupMotor Alarm
| AHU controller | Alarm | Special | AggBlKAlr |  | 1x0331 | 6.54 | BI312 | 6.54 | 0 | 1 |  |  |  | Start of AHU is blocked, if mounted and open
| Heating Coil #1 or #2 | Fire | Special | FireEHtCoilAlr |  | 1x0332 | 6.54 | BI313 | 6.54 | 0 | 1 |  |  |  | Firethermostat alarm via Digital Input "Electric heating coil, fire thermostat"
| Heating Coil Pre-Heater | Fire | Special | FireEPrHeatAlr |  | 1x0333 | 6.54 | BI314 | 6.54 | 0 | 1 |  |  |  | Firethermostat alarm via Digital Input "El pre-heating coil, fire thermostat"
0x13A0 | Heating coil 2, Water | Alarm | Standard | HW2SensErr |  | 1x0150 | x.xx | BI86 | x.xx | 0 | 1 |  | HeatWaterTemp -Sensor Error | Varmeflade 2; Returføler -Følerfejl | Heating coil 2 - Return sensor - Sensor fault
0x13A1 | Heating coil 2, Water | Alarm | Standard | HW2FrostAlr |  | 1x0151 | x.xx | BI87 | x.xx | 0 | 1 |  | HeatWaterTemp -FrostReg Alarm | Varmeflade 2; Frost Alarm | Heating coil 2 - Frost alarm
0x13A2 | Heating coil 2, Water | Status | Standard | HW2FrostReg |  | 1x0152 | x.xx | BI84 | x.xx | 0 | 1 |  | HeatWaterTemp -FrostReg Active | Varmeflade 2; Frostregulering Aktiv | Heating coil 2 - Frost control active
0x13A3 | Heating coil 2, Water | Status | Standard | HW2PumpExer |  | 1x0153 | x.xx | BI85 | x.xx | 0 | 1 |  | HeatWater PumpExercise active | Varmeflade 2; Cirkulationspumpe, pumpemotion aktiv | Heating coil 2 - Circulation pump, pump exercising active
0x1401 | Heater coil 2 | Status | Standard | Heat_RE2 |  | 1x0154 | x.xx | BI278 | 4.22 | 0 | 1 |  | Heat Relay 2 (ExtMod-Reserve) | Varmerelæ 2 (ExtMod-Reserve) | Heating relay 2 (ExtMod-Reserve)
0x1404 | Heating coil 2, Electric | Status | Special | Heat_RE21 |  | 1x0155 | x.xx | BI212 | x.xx | 0 | 1 |  | Heat2 Relay 21 (ExtMod-Reserve) | Varmerelæ 21 (ExtMod-Reserve) | Heating relay 21 (ExtMod-Reserve)
0x1405 | Heating coil 2, Electric | Status | Special | Heat_RE22 |  | 1x0156 | x.xx | BI213 | x.xx | 0 | 1 |  | Heat2 Relay 22 (ExtMod-Reserve) | Varmerelæ 22 (ExtMod-Reserve) | Heating relay 22 (ExtMod-Reserve)
0x1406 | Heating coil 2, Electric | Status | Special | Heat_RE23 |  | 1x0157 | x.xx | BI214 | x.xx | 0 | 1 |  | Heat2 Relay 23 (ExtMod-Reserve) | Varmerelæ 23 (ExtMod-Reserve) | Heating relay 23 (ExtMod-Reserve)
0x1407 | Heating coil 2, Electric | Status | Special | Heat_RE24 |  | 1x0159 | x.xx | BI215 | x.xx | 0 | 1 |  | Heat2 Relay 24 (ExtMod-Reserve) | Varmerelæ 24 (ExtMod-Reserve) | Heating relay 24 (ExtMod-Reserve)
0x1408 | Heating coil 2, Electric | Status | Special | Heat_RE25 |  | 1x0160 | x.xx | BI216 | x.xx | 0 | 1 |  | Heat2 Relay 25 (ExtMod-Reserve) | Varmerelæ25 (ExtMod-Reserve) | Heating relay 25 (ExtMod-Reserve)
0x1110 | Temp. sensor | Alarm | Special | AddOnTSens1Err |  | 1x0161 | x.xx | BI79 | x.xx | 0 | 1 |  | Additional TempSensor -Error | Tillægsføler 1 - Følerfejl | Add on sensor 1 - Sensor fault
0x1111 | Temp. sensor | Alarm | Special | AddOnTSens2Err |  | 1x0162 | x.xx | BI80 | x.xx | 0 | 1 |  | Additional TempSensor -Error | Tillægsføler 2 - Følerfejl | Add on sensor 2 - Sensor fault
0x1112 | Temp. sensor | Alarm | Special | AddOnTSens3Err |  | 1x0163 | x.xx | BI81 | x.xx | 0 | 1 |  | Additional TempSensor -Error | Tillægsføler 3 - Følerfejl | Add on sensor 3 - Sensor fault
0x1113 | Temp. sensor | Alarm | Special | AddOnTSens4Err |  | 1x0164 | x.xx | BI82 | x.xx | 0 | 1 |  | Additional TempSensor -Error | Tillægsføler 4 - Følerfejl | Add on sensor 4 - Sensor fault
0x140B | Heating coil 1, Water | Alarm | Standard | HW_StatLuftAlr |  | 1x0165 | x.xx | BI302 | 6.51 | 0 | 1 |  | Status Luft Alarm input | Status Frosttermostat Alarm (Digital input) | Status frost thermostat alarm (digital input)
0x1E9C | Heat exchanger | Alarm | Standard | AlrFrzBattEXC |  | 1x0166 | x.xx | BI100 | x.xx | 0 | 1 |  | Frostalarm CoilEXC | Frostalarm væskekoblet flade (CoilEXC) | Frost alarm fluid-coupled coil (CoilEXC)
0x1459 | Humidifier | Alarm | Standard | HumidAlrInp |  | 1x0169 | x.xx | BI303 | 6.51 | 0 | 1 |  | Huminifier Alarm Status | Befugter Alarm Status | Humidifier alarm status
0x13C0 | Combi coil | Alarm | Standard | CombiTSenErr |  | 1x0170 | x.xx | BI279 | 4.22 | 0 | 1 |  | CombiCoilTemp -Sensor Error | Kombiflade; Returføler -Følerfejl | Combi coil - Return sensor - Sensor fault
0x13C1 | Combi coil | Alarm | Standard | CombiFrostAlrH |  | 1x0171 | x.xx | BI280 | 4.22 | 0 | 1 |  | CombiHeatWaterTemp -FrostReg Alarm | Kombiflade; Frost Alarm | Combi coil - Frost alarm
0x13C2 | Combi coil | Status | Standard | CombiFrostReg |  | 1x0172 | x.xx | BI281 | 4.22 | 0 | 1 |  | HeatWaterTemp -FrostReg Active | Kombiflade; Frostregulering Aktiv | Combi coil - Frost protection active
0x13C3 | Combi coil | Status | Standard | CombiPumpExer |  | 1x0173 | x.xx | BI282 | 4.22 | 0 | 1 |  | HeatWater PumpExercise active | Kombiflade; Cirkulationspumpe, pumpemotion aktiv | Combi coil - Circulation pump, pump exercising active
0x13C5 | Combi coil | Status | Standard | CombiCoolRel |  | 1x0174 | x.xx | BI283 | 4.22 | 0 | 1 |  | Combicoil CoolRelay | Kombiflade; Kølerelæ aktiv | Combi coil; Cooling relay aktive
0x13C4 | Combi coil | Status | Standard | CombiHeatRel |  | 1x0175 | x.xx | BI284 | 4.22 | 0 | 1 |  | Combicoil HeatRelay | Kombiflade; Varmerelæ aktiv | Combi coil; Heating relay aktive
0x1126 | Heating coil 2 | Status | Special | Ht2DelayStatus |  | 1x0176 | x.xx | BI113 | x.xx | 0 | 1 |  | Status of delaytimer Heat 2 | Status timer Varme2 | Special customer code: Status timer Heat2
0x1127 | Heating coil 2 | Status | Special | Ht2RecBlkAct |  | 1x0177 | x.xx | BI115 | x.xx | 0 | 1 |  | Blocking of heat2 under recirce active | Blokering af Varme2 ved omluft = Aktiv | Special customer code: Blokcing Heat2 in recirkulation mode = Aktivated
0x1128 | Heating coil 2 | Status | Special | Ht2FlowChgAct |  | 1x0178 | x.xx | BI112 | x.xx | 0 | 1 |  | Flow is change heat2 active | Flow ændret p.g.a. Varme2 er aktiv | Special customer code: Flow changed caused Heat2 is aktivated
0x1129 | Damper, Recirculation | Status | Special | IntRecFlowStat |  | 1x0179 | x.xx | BI116 | x.xx | 0 | 1 |  | Status of low flow under 100% recirce | Status lavt flow under 100% omluft | Special customer code: Status low flow during 100% recirkulation
0x112A | Damper, Recirculation | Status | Special | RecClosDmpAct |  | 1x0180 | x.xx | BI117 | x.xx | 0 | 1 |  | Recirculation damper is closed | Omluftspjæld er lukket | Special customer code: Recirkulation damper is closed
0x1120 | Heating coil 2 | Status | Special | HT2DelLimBlkNo |  | 1x0181 | x.xx | BI114 | x.xx | 0 | 1 |  | Limit of heat 2 is avoid | Begrænsning af Varme2 er ikke aktiv | Special customer code: Limitting Heat2 is not activated
0x1121 | AHU controller | Status | Special | NO_CStopStat |  | 1x0182 | x.xx | BI304 | 6.51 | 0 | 1 |  | Freshair cool stop active | Friskluftkøling stop aktiv | Special customer code: Outsdoor air cooling: Stop activated
0x1338 | Heating coil 1 | Status | Special | HW1RiFaActiv |  | 1x0183 | x.xx | BI118 | x.xx | 0 | 1 |  | RiseFall is active | Max. stige-/falde-tid er aktiveret | Max. raise-/fall-time is aktivated
0x1447 | Damper, Smoke evac. | Alarm | Special | Alr_FireEvaDmp |  | 1x0184 | x.xx | BI277 | 4.22 | 0 | 1 |  | Alarm with smoke evacuation damper active | Alarm hvor røg-evakueringsspjæld er aktiv | Alarm smoke evacuation damper is activated ("1" = Open damper)
0x1990 | Fan, Supply drive 2 | Alarm | Special | EC2supMtAlrVlo |  | 1x0185 | x.xx | BI120 | x.xx | 0 | 1 |  | EC2-SupplyMotor2 Vlo Alarm | EC 2-Tilluftsmotor spænding lav alarm | OJ-EC/-DV 2-supply air motor voltage low alarm
0x1991 | Fan, Supply drive 2 | Alarm | Special | EC2supMtAlrVhi |  | 1x0186 | x.xx | BI121 | x.xx | 0 | 1 |  | EC2-SupplyMotor Vhi Alarm | EC 2-Tilluftsmotor spænding høj alarm | OJ-EC/-DV 2-supply air motor voltage high alarm
0x1992 | Fan, Supply drive 2 | Alarm | Special | EC2supMtAlrIhi |  | 1x0187 | x.xx | BI122 | x.xx | 0 | 1 |  | EC2-SupplyMotor Ihi Alarm | EC 2-Tilluftsmotor høj strømgrænse alarm | OJ-EC/-DV 2-supply air motor high current limit alarm
0x1993 | Fan, Supply drive 2 | Alarm | Special | EC2supMtAlrTmp |  | 1x0188 | x.xx | BI123 | x.xx | 0 | 1 |  | EC2-SupplyMotor Temp Alarm | EC 2-Tilluftsmotor temperatur alarm | OJ-EC/-DV 2-supply air motor temperature alarm
0x1994 | Fan, Supply drive 2 | Alarm | Special | EC2supMtAlrPhs |  | 1x0189 | x.xx | BI124 | x.xx | 0 | 1 |  | EC2-SupplyMotor Phase Alarm | EC 2-Tilluftsmotor alarm for fasefejl | OJ-EC/-DV 2-supply air motor alarm for phase error
0x1995 | Fan, Supply drive 2 | Alarm | Special | EC2supRotBlok |  | 1x0190 | x.xx | BI126 | x.xx | 0 | 1 |  | EC2-SupplyMotor Blocked Alarm | EC 2-Tilluftsmotor alarm for blokeret rotor | OJ-EC/-DV 2-supply air motor alarm for blocked rotor
0x1996 | Fan, Supply drive 2 | Alarm | Special | EC2supMtIhiLim |  | 1x0191 | x.xx | BI119 | x.xx | 0 | 1 |  | EC2-SupplyMotor I Hi Limit | EC 2-Tilluftsmotor høj strøm Grænse; kortslutningsbeskyttelse | OJ-EC/-DV 2-supply/supply air motor high current limit; shortcuit protection
0x19B0 | Fan, Extract drive 2 | Alarm | Special | EC2extMtAlrVlo |  | 1x0192 | x.xx | BI128 | x.xx | 0 | 1 |  | EC-ExtractMotor Vlo Alarm | EC 2-Fraluftsmotor spænding lav alarm | OJ-EC/-DV 2-extract/exhaust motor voltage low alarm
0x19B1 | Fan, Extract drive 2 | Alarm | Special | EC2extMtAlrVhi |  | 1x0193 | x.xx | BI129 | x.xx | 0 | 1 |  | EC-ExtractMotor Vhi Alarm | EC 2-Fraluftsmotor spænding høj alarm | OJ-EC/-DV 2-extract/exhaust motor voltage high alarm
0x19B2 | Fan, Extract drive 2 | Alarm | Special | EC2extMtAlrIhi |  | 1x0194 | x.xx | BI130 | x.xx | 0 | 1 |  | EC-ExtractMotor Ihi Alarm | EC 2-Fraluftsmotor høj strømgrænse alarm | OJ-EC/-DV 2-extract/exhaust motor high current limit alarm
0x19B3 | Fan, Extract drive 2 | Alarm | Special | EC2extMtAlrTmp |  | 1x0195 | x.xx | BI131 | x.xx | 0 | 1 |  | EC-ExtractMotor Temp Alarm | EC 2-Fraluftsmotor temperatur alarm | OJ-EC/-DV 2-extract/exhaust motor temperature alarm
0x19B4 | Fan, Extract drive 2 | Alarm | Special | EC2extMtAlrPhs |  | 1x0196 | x.xx | BI132 | x.xx | 0 | 1 |  | EC-ExtractMotor Phase Alarm | EC 2-Fraluftsmotor alarm for fasefejl | OJ-EC/-DV 2-extract/exhaust motor alarm for phase error
0x19B5 | Fan, Extract drive 2 | Alarm | Special | EC2extRotBlok |  | 1x0197 | x.xx | BI134 | x.xx | 0 | 1 |  | EC-ExtractMotor V Ripple Alarm | EC 2-Fraluftsmotor alarm for blokeret rotor | OJ-EC/-DV 2-extract/exhaust motor alarm for blocked rotor
0x19B6 | Fan, Extract drive 2 | Alarm | Special | EC2extMtIhiLim |  | 1x0198 | x.xx | BI127 | x.xx | 0 | 1 |  | EC-ExtractMotor I Hi Limit | EC 2-Fraluftsmotor høj strøm Grænse; kortslutningsbeskyttelse | OJ-EC/-DV 2-extract/exhaust motor high current limit; shortcuit protection
0x1EA6 | Temp. sensor | Alarm | Standard | AlrTTH6202Com |  | 1x0199 | x.xx | BI155 | x.xx | 0 | 1 |  | TTH6202 Communication Alarm | TTH-6202 kommunikationsfejl | TTH-6202 communication error
0x1950 | Fan, Supply drive | Alarm | Standard | ECsupMtrAlrVlo |  | 1x0200 | x.xx | BI138 | x.xx | 0 | 1 |  | EC-SupplyMotor Vlo Alarm | EC-Tilluftsmotor spænding lav alarm | OJ-EC/-DV-supply air motor voltage low alarm
0x1951 | Fan, Supply drive | Alarm | Standard | ECsupMtrAlrVhi |  | 1x0201 | x.xx | BI139 | x.xx | 0 | 1 |  | EC-SupplyMotor Vhi Alarm | EC-Tilluftsmotor spænding høj alarm | OJ-EC/-DV-supply air motor voltage high alarm
0x1952 | Fan, Supply drive | Alarm | Standard | ECsupMtrAlrIhi |  | 1x0202 | x.xx | BI140 | x.xx | 0 | 1 |  | EC-SupplyMotor Ihi Alarm | EC-Tilluftsmotor høj strømgrænse alarm | OJ-EC/-DV-supply air motor high current limit alarm
0x1953 | Fan, Supply drive | Alarm | Standard | ECsupMtrAlrTmp |  | 1x0203 | x.xx | BI141 | x.xx | 0 | 1 |  | EC-SupplyMotor Temp Alarm | EC-Tilluftsmotor temperatur alarm | OJ-EC/-DV-supply air motor temperature alarm
0x1954 | Fan, Supply drive | Alarm | Standard | ECsupMtrAlrPhs |  | 1x0204 | x.xx | BI142 | x.xx | 0 | 1 |  | EC-SupplyMotor Phase Alarm | EC-Tilluftsmotor alarm for fasefejl | OJ-EC/-DV-supply air motor alarm for phase error
0x1955 | Fan, Supply drive | Alarm | Standard | ECsupRotBloked |  | 1x0205 | x.xx | BI144 | x.xx | 0 | 1 |  | EC-SupplyMotor Blocked Alarm | EC-Tilluftsmotor alarm for blokeret rotor | OJ-EC/-DV-supply air motor alarm for blocked rotor
0x1956 | Fan, Supply drive | Alarm | Standard | ECsupMtrIhiLim |  | 1x0206 | x.xx | BI137 | x.xx | 0 | 1 |  | EC-SupplyMotor I Hi Limit | EC-Tilluftsmotor høj strøm Grænse; kortslutningsbeskyttelse | OJ-EC/-DV-supply air motor high current limit; shortcuit protection
0x1970 | Fan, Extract drive | Alarm | Standard | ECextMtrAlrVlo |  | 1x0207 | x.xx | BI146 | x.xx | 0 | 1 |  | EC-ExtractMotor Vlo Alarm | EC-Fraluftsmotor spænding lav alarm | OJ-EC/-DV-extract/exhaust motor voltage low alarm
0x1971 | Fan, Extract drive | Alarm | Standard | ECextMtrAlrVhi |  | 1x0208 | x.xx | BI147 | x.xx | 0 | 1 |  | EC-ExtractMotor Vhi Alarm | EC-Fraluftsmotor spænding høj alarm | OJ-EC/-DV-extract/exhaust motor voltage high alarm
0x1972 | Fan, Extract drive | Alarm | Standard | ECextMtrAlrIhi |  | 1x0209 | x.xx | BI148 | x.xx | 0 | 1 |  | EC-ExtractMotor Ihi Alarm | EC-Fraluftsmotor høj strømgrænse alarm | OJ-EC/-DV-extract/exhaust motor high current limit alarm
0x1973 | Fan, Extract drive | Alarm | Standard | ECextMtrAlrTmp |  | 1x0210 | x.xx | BI149 | x.xx | 0 | 1 |  | EC-ExtractMotor Temp Alarm | EC-Fraluftsmotor temperatur alarm | OJ-EC/-DV-extract/exhaust motor temperature alarm
0x1974 | Fan, Extract drive | Alarm | Standard | ECextMtrAlrPhs |  | 1x0211 | x.xx | BI150 | x.xx | 0 | 1 |  | EC-ExtractMotor Phase Alarm | EC-Fraluftsmotor alarm for fasefejl | OJ-EC/-DV-extract/exhaust motor alarm for phase error
0x1975 | Fan, Extract drive | Alarm | Standard | ECextRotBloked |  | 1x0212 | x.xx | BI152 | x.xx | 0 | 1 |  | EC-ExtractMotor V Ripple Alarm | EC-Fraluftsmotor alarm for blokeret rotor | OJ-EC/-DV-extract/exhaust motor alarm for blocked rotor
0x1976 | Fan, Extract drive | Alarm | Standard | ECextMtrIhiLim |  | 1x0213 | x.xx | BI145 | x.xx | 0 | 1 |  | EC-ExtractMotor I Hi Limit | EC-Fraluftsmotor høj strøm Grænse; kortslutningsbeskyttelse | OJ-EC/-DV-extract/exhaust motor high current limit; shortcuit protection
0x1E35 | IO Extension module | Alarm | Standard | AlrExtIO1_Comm |  | 1x0214 | x.xx | BI158 | x.xx | 0 | 1 |  | External IO-Modul-1 Comm Alarm | Extern IO-Modul no. 1 - kommunikationsfejl | Extention IO-Modul no. 1 - communication error
0x1E36 | IO Extension module | Alarm | Standard | AlrExtIO2_Comm |  | 1x0215 | x.xx | BI159 | x.xx | 0 | 1 |  | External IO-Modul-2 Comm Alarm | Extern IO-Modul no. 2 - kommunikationsfejl | Extention IO-Modul no. 2 - communication error
0x1E84 | IO Extension module | Alarm | Standard | AlrExtIO3_Comm |  | 1x0216 | x.xx | BI160 | x.xx | 0 | 1 |  | External IO-Modul-3 Comm Alarm | Extern IO-Modul no. 3 - kommunikationsfejl | Extention IO-Modul no. 3 - communication error
0x1E85 | IO Extension module | Alarm | Standard | AlrExtIO4_Comm |  | 1x0217 | x.xx | BI161 | x.xx | 0 | 1 |  | External IO-Modul-4 Comm Alarm | Extern IO-Modul no. 4 - kommunikationsfejl | Extention IO-Modul no. 4 - communication error
0x1E86 | IO Extension module | Alarm | Standard | AlrExtIO5_Comm |  | 1x0218 | x.xx | BI162 | x.xx | 0 | 1 |  | External IO-Modul-5 Comm Alarm | Extern IO-Modul no. 5 - kommunikationsfejl | Extention IO-Modul no. 5 - communication error
0x1E87 | IO Extension module | Alarm | Standard | AlrExtIO6_Comm |  | 1x0219 | x.xx | BI163 | x.xx | 0 | 1 |  | External IO-Modul-6 Comm Alarm | Extern IO-Modul no. 6 - kommunikationsfejl | Extention IO-Modul no. 6 - communication error
0x1E88 | IO Extension module | Alarm | Standard | AlrExtIO7_Comm |  | 1x0220 | x.xx | BI164 | x.xx | 0 | 1 |  | External IO-Modul-7 Comm Alarm | Extern IO-Modul no. 7 - kommunikationsfejl | Extention IO-Modul no. 7 - communication error
0x1E8F | IO Extension module | Alarm | Standard | AlrExtIO8_Comm |  | 1x0221 | x.xx | BI165 | x.xx | 0 | 1 |  | External IO-Modul-8 Comm Alarm | Extern IO-Modul no. 8 - kommunikationsfejl | Externalal IO-Modul no. 8 - communication error
0x1EA9 | Temp. sensor | Alarm | Special | AlrAddOnSens1 |  | 1x0222 | x.xx | BI167 | x.xx | 0 | 1 |  | Sensor alarm addon 1 | Tillægsføler 1 - Følerfejl | Addon sensor 1 - Sensor error
0x1EAA | Temp. sensor | Alarm | Special | AlrAddOnSens2 |  | 1x0223 | x.xx | BI168 | x.xx | 0 | 1 |  | Sensor alarm addon 2 | Tillægsføler 2 - Følerfejl | Addon sensor 2 - Sensor error
0x1EAB | Temp. sensor | Alarm | Special | AlrAddOnSens3 |  | 1x0224 | x.xx | BI169 | x.xx | 0 | 1 |  | Sensor alarm addon 3 | Tillægsføler 3 - Følerfejl | Addon sensor 3 - Sensor error
0x1EAC | Temp. sensor | Alarm | Special | AlrAddOnSens4 |  | 1x0225 | x.xx | BI170 | x.xx | 0 | 1 |  | Sensor alarm addon 4 | Tillægsføler 4 - Følerfejl | Addon sensor 4 - Sensor error
0x03BA | Cooling, DX | Status | Special | ROHRiFaActiv |  | 1x0226 | x.xx | BI174 | x.xx | 0 | 1 |  | Flag for Rise-Falltime active DX-CO2-Cooling | Kundespecifik | Special customer code functionality
0x0436 | Combi coil | Status | Standard | CmbEnCtrlMB |  | NA | x.xx | BI175 | 4.18 | 0 | 1 | 0 | CombiCoil enable Heat/Cool ctrl via MB | KombiFlade frigiv Varme/Køl til styring ModBus | CombiCoil enable Heat/Cool ctrl via MB
0x13C9 | Combi coil | Status | Standard | Cmb2CoolRel |  | 1x0227 | x.xx | BI173 | x.xx | 0 | 1 |  | Combicoil 2. CoolRelay | Kombiflade; Kølerelæ no. 2 aktiv | Combi coil; Cooling relay no. 2 aktive
0x1959 | Fan, Supply drive | Alarm | Standard | ECsupEEP_Err |  | 1x0228 | x.xx | BI178 | x.xx | 0 | 1 |  | EC-SupplyMotor EEprom error | Tilluft ventilator Eeprom fejl | Supply air fan EEprom error
0x1999 | Fan, Supply drive 2 | Alarm | Special | EC2supEEP_Err |  | 1x0229 | x.xx | BI179 | x.xx | 0 | 1 |  | EC2-SupplyMotor EEprom error | Tilluft ventilator 2 Eeprom fejl | Supply air fan 2 EEprom error
0x1979 | Fan, Extract drive | Alarm | Standard | ECextEEP_Err |  | 1x0230 | x.xx | BI180 | x.xx | 0 | 1 |  | EC-ExtractMotor EEprom error | Fraluft ventilator Eeprom fejl | Exhaust air fan EEprom error
0x19B9 | Fan, Extract drive 2 | Alarm | Special | EC2extEEP_Err |  | 1x0231 | x.xx | BI181 | x.xx | 0 | 1 |  | EC-ExtractMotor EEprom error | Fraluft ventilator 2 Eeprom fejl | Exhaust air fan 2 EEeprom error
0x1EAD | Temp. sensor | Alarm | Standard | TTH6040ComAlr |  | 1x0232 | x.xx | BI182 | x.xx | 0 | 1 |  | Sensor alarm TTH6040 no Com | TTH-6040 kommunikationsfejl | TTH-6040 communikation error
0x1EAE | Cooling, DX | Alarm | Special | LowOilDXHPAlr |  | 1x0233 | x.xx | BI183 | x.xx | 0 | 1 |  | Sensor alarm low oil level | Lav olieniveau kølekompressor | Low oil level cooling compressor
0x1EAF | AHU controller | Fire | Standard | AlrFireManStop |  | 1x0234 | x.xx | BI203 | x.xx | 0 | 1 |  | Firemanstop is active | Brandmand stop | Fire mann stop
0x1EB0 | Damper, Smoke evac. | Smoke | Standard | AlrSmokEvac |  | 1x0235 | x.xx | BI204 | x.xx | 0 | 1 |  | Mode 304, Smoke evacuation ext. Fan | Røg-evakuering aktiv | Smoke evacuation activated
0x1EB1 | Temp. Room | Alarm | Standard | BMSRoomTOOR |  | 1x0236 | x.xx | BI201 | x.xx | 0 | 1 |  | BMS-Sensor Room Out of Range | BMS rumføler udenfor område | BMS room sensor out of range
0x1EB2 | Temp. Out door | Alarm | Standard | BMSOutDTOOR |  | 1x0237 | x.xx | BI202 | x.xx | 0 | 1 |  | BMS-Sensor Outdoor Out of Range | BMS udetemperatur udenfor område | BMS outdoor temperature out of range
0x1EB3 | Fan, Smoke evac. | Alarm | Standard | AlrSmokEvaFan |  | 1x0238 | x.xx | BI205 | x.xx | 0 | 1 |  | alarm from Smoke eva fan | Røg-evakueringsventiltor alarm | Smoke evacuation fan alarm
|  |  | Standard | TTH6040OutDAlr |  | 1x0239 | 6.51 | BI294 | 6.51 | 0 | 1 |  |  |  | Sensor alarm TTH6040 OutDoor no Com (port A)
0x1015 | Damper, Fresh air | Status | Standard | StatInleRel |  | 1x0240 | x.xx | BI206 | x.xx | 0 | 1 |  | Big Damper relay supply | Udgang for udeluft/afkastspjæld aktiv | Output for outdoor air/exhaust air active ("1" = Open damper)
0x1016 | Damper, Supply air | Status | Standard | StatSupRel |  | 1x0241 | x.xx | BI207 | x.xx | 0 | 1 |  | Big Damper relay Supply | Udgang for tilluftsspjæld aktiv | Output for supply air damper aktive
0x1017 | Damper, Recirculation | Status | Standard | StatRecRel |  | 1x0242 | x.xx | BI208 | x.xx | 0 | 1 |  | Big Damper relay Recirce | Udgang for recirkuleringsspjæld aktiv | Output for recircutation damper aktive ("1" = Open damper)
0x1301 | Temp. Out door | Alarm | Standard | ExOutDSensErr |  | 1x0243 | x.xx | BI209 | x.xx | 0 | 1 |  | External OutDoorTemp -Sensor Error | Ekstern udeføler - følerfejl | External outdoor temperature sensor - sensor error
0x1290 | Preheater coil, water | Alarm | Standard | PHTempSensErr |  | 1x0244 | x.xx | BI210 | x.xx | 0 | 1 |  | Temp sensor error | Temperaturføler forvarmeflade - følerfejl | Temperature sensor pre-heater - sensor error
0x1351 | Cooling coil | Alarm | Standard | CW_TSensErr |  | 1x0245 | x.xx | BI211 | x.xx | 0 | 1 |  | CWB Temperature Sens Error | Kølevand fremløb - følerfejl | Cooling water supply temperature - sensor error
0x1409 | Heating coil 1, Electric | Status | Standard | Heat_RE26 |  | 1x0246 | x.xx | BI217 | x.xx | 0 | 1 |  | Heat2 Relay 26 (ExtMod-Reserve) | Varmerelæ26 (ExtMod-Reserve) | Heating relay26 (ExtMod-Reserve)
0x140A | Combi coil | Status | Standard | Combi_PumpRE |  | 1x0247 | x.xx | BI218 | x.xx | 0 | 1 |  | Combicoil Relay Pump | Pumperelæ combiflade aktiveret | Pump relay combi coil activated
0x1486 | Heating coil 2, Electric | Alarm | Standard | EL2_OverHtBac |  | 1x0248 | x.xx | BI221 | x.xx | 0 | 1 |  | ElCoil2 Overheat State to Bacnet | EL-varmeflade 2; Overhedning | Electric coil 2: High temperature alarm signal
0x1EC4 | Heating coil 2, Electric | Alarm | Standard | AlrBat2Contact |  | 1x0249 | x.xx | BI222 | x.xx | 0 | 1 |  | Heat2 El-coil, Contactor is stuck alarm | EL-varmeflade 2; Kontaktor hænger | Electric coil 2: Relay stuck
0x1EB4 | Filter | Alarm | Standard | OutFiltAlrOn |  | 1x0250 | x.xx | BI223 | x.xx | 0 | 1 |  | alarm from Outdoorfiltertimer | Alarm - Timer for filterskift tilluft udløbet | Alarm - Time is out for filter change supply air filter
0x1EB5 | Filter | Alarm | Standard | ExtFiltAlrOn |  | 1x0251 | x.xx | BI224 | x.xx | 0 | 1 |  | alarm from Extractfiltertimer | Alarm - Timer for filterskift fraluft udløbet | Alarm - Time is out for filter change exhaust air filter
0x0392 | Filter | Calibration | Standard | FiltCaliDone |  | NA | NA | BI227 | x.xx | 0 | 1 | 0 | Filter Calibration done (valid filterpress data) DYNAMICMODE ONLY | Filter Kalibrering gennemført (valide filter trykdata) O328 | Filter Calibration done (valid filterpress data) DYNAMICMODE ONLY
0x0812 | Fan | Speed | Standard | ExtDrfMePeriod |  | NA | NA | BI228 | x.xx | 0 | 1 | 0 | Extended Periode = Med-Speed (High / Med OFF -> LO-Speed) | Forceret drift Medium (register 0x0010 skal være aktiv) Midlertidig overstyring af urdrift. | Input for forced medium speed
0x1EB6 | Fan, Supply drive | Alarm | Standard | FCAlrSupPoLim |  | 1x0252 | x.xx | BI229 | x.xx | 0 | 1 |  | Powerlimit active from DV FC Supply | Alarm - tilluftventilator, effektgrænse | Alarm - Supply air fan, Power limit
0x1EB7 | Fan, Extract drive | Alarm | Standard | FCAlrExtPoLim |  | 1x0253 | x.xx | BI230 | x.xx | 0 | 1 |  | Powerlimit active from DV FC Extract | Alarm - fraluftventilator, effektgrænse | Alarm - Exhaust air fan, Power limit
0x1EBE | Fan, Supply drive | Alarm | Standard | FCAlrSupDVRBlk |  | 1x0254 | x.xx | BI231 | x.xx | 0 | 1 |  | Rotor Blocked alarm from DV FC Supply | Alarm - tilluftventilator, DV-FC rotor blokkeret | Alarm - Supply air fan DV-FC Rotor bloked
0x1EBF | Fan, Extract drive | Alarm | Standard | FCAlrExtDVRBlk |  | 1x0255 | x.xx | BI232 | x.xx | 0 | 1 |  | Rotor Blocked alarm from DV FC Extract | Alarm - fraluftventilator, DV-FC rotor blokkeret | Alarm - Exhaust air fan, DV-FC Rotor bloked
0x1F00 | Fan, Supply drive | Alarm | Standard | DVAlrSupIStop |  | 1x0256 | x.xx | BI233 | x.xx | 0 | 1 |  | Intern Stop alarm from DV Supply | Alarm - tilluftventilator1, høj strømgrænse stop | Alarm - Supply air fan1, High Current Stop
0x1F02 | Fan, Supply drive 2 | Alarm | Standard | DV2AlrSupIStop |  | 1x0257 | x.xx | BI235 | x.xx | 0 | 1 |  | Intern Stop alarm from DV Supply 2 | Alarm - tilluftventilator2, høj strømgrænse stop | Alarm - Supply air fan2, High Current Stop
0x1F01 | Fan, Extract drive | Alarm | Standard | DVAlrExtIStop |  | 1x0258 | x.xx | BI234 | x.xx | 0 | 1 |  | Intern Stop alarm from DV Extract | Alarm - fraluftventilator1, høj strømgrænse stop | Alarm - Exhaust air fan1, High Current Stop
0x1F03 | Fan, Extract drive 2 | Alarm | Standard | DV2AlrExtIStop |  | 1x0259 | x.xx | BI236 | x.xx | 0 | 1 |  | Intern Stop alarm from DV Extract 2 | Alarm - fraluftventilator2, høj strømgrænse stop | Alarm - Exhaust air fan2, High Current Stop
0x13CE | Combi coil | Status | Standard | CmbHeatState |  | 1x0260 | x.xx | BI237 | x.xx | 0 | 1 |  | Combicoil heat usable | Status kombiflade = Varme | Status combi coil = Heating
0x13CF | Combi coil | Status | Standard | CmbCoolState |  | 1x0261 | x.xx | BI238 | x.xx | 0 | 1 |  | Combicoil cool usable | Status kombiflade = Køle | Status combi coil = Heating
0x1487 | Preheater coil, electric | Alarm | Standard | Pre_OverHtBac |  | 1x0262 | x.xx | BI239 | x.xx | 0 | 1 |  | ElPrehheat Overheat State to Bacnet | Alarm = overhedning forvarmeflade | Alarm = over heating pre-heater
0x1E90 | Preheater coil, electric | Alarm | Standard | AlrPrhContact |  | 1x0263 | x.xx | BI240 | x.xx | 0 | 1 |  | Contact error Preheater El-coil | Alarm = relæ hænger forvarmeflade | Alarm = preheater relay hanging
0x19CA | Fan, Supply drive | Alarm | Standard | ECSupHiIOAlr |  | 1x0264 | x.xx | BI241 | x.xx | 0 | 1 |  | EC Supply Hi Curr Alr | Alarm EC tilluft = Høj IO strøm | Alarm OJ-EC/-DV supply air = High IO current
0x19CB | Fan, Extract drive | Alarm | Standard | ECExtHiIOAlr |  | 1x0265 | x.xx | BI242 | x.xx | 0 | 1 |  | EC Extract Hi Curr Alr | Alarm EC fraluft = Høj IO strøm | Alarm OJ-EC/-DV extract air = High IO current
0x19CC | Fan, Supply drive 2 | Alarm | Special | EC2SupHiIOAlr |  | 1x0266 | x.xx | BI243 | x.xx | 0 | 1 |  | EC2 Supply Hi Curr Alr | Alarm EC2 tilluft = Høj IO strøm | Alarm OJ-EC/-DV2 supply air = High IO current
0x19CD | Fan, Extract drive 2 | Alarm | Special | EC2ExtHiIOAlr |  | 1x0267 | x.xx | BI244 | x.xx | 0 | 1 |  | EC2 Extract Hi Curr Alr | Alarm EC2 fraluft = Høj IO strøm | Alarm OJ-EC/-DV2 extract air = High IO current
| CVM Mini Meter | Alarm | Standard | AlrCommCVMMini |  | 1x0268 | 4.21 | BI305 | 6.51 | 0 | 1 |  |  |  | Communication CVM Mini Meter
| CVM Mini Meter | Alarm | Standard | AlrCommCVMCool |  | 1x0269 | 4.21 | BI306 | 6.51 | 0 | 1 |  |  |  | Communication CVM Mini Cool Meter
0x19CE | Fan, supply | Alarm | Standard | AlrSupFanStop |  | 1x0270 | 4.18 | BI245 | 4.18 | 0 | 1 |  | B-Alr SupFan is stopped | B-Alarm Tilluft ventilator kører ikke | B-Alr SupFan is stopped
0x19CF | HMI display | Alarm | Standard | AlrComHMI20 |  | 1x0271 | 4.18 | BI307 | 6.51 | 0 | 1 |  | A-Alr Comm Error HMI20 | A-Alarm Fælles Alarm HMI20 | A-Alr Comm Error HMI20
0x19D6 | Damper, Smoke evac. | Alarm | Special | AlrSMEvacDmp |  | 1x0272 | 4.18 | BI246 | 4.18 | 0 | 1 |  | Smoke Evac Damper not in position | RøgEvakueringsSpjæld har ikke opnår ønsket position | Smoke Evac Damper not in position
0x19D7 | Damper, Smoke evac. | Alarm | Special | AlrSMBPassDmp |  | 1x0273 | 4.18 | BI247 | 4.18 | 0 | 1 |  | Smoke Bypass Damper not in position | RøgBypassSpjæld har ikke opnår ønsket position | Smoke Bypass Damper not in position
0x1F20 | Pressure | Alarm | Standard | DPTH_1ComAlr |  | 1x0274 | 4.18 | BI248 | 4.18 | 0 | 1 |  | Communication Alarm DPTH1 | Kommunikation Alarm DPTH1 | Communication Alarm DPTH1
0x1F21 | Pressure | Alarm | Standard | DPTH_2ComAlr |  | 1x0275 | 4.18 | BI249 | 4.18 | 0 | 1 |  | Communication Alarm DPTH2 | Kommunikation Alarm DPTH2 | Communication Alarm DPTH2
0x1F22 | Pressure | Alarm | Standard | DPTH_3ComAlr |  | 1x0276 | 4.18 | BI250 | 4.18 | 0 | 1 |  | Communication Alarm DPTH3 | Kommunikation Alarm DPTH3 | Communication Alarm DPTH3
0x1F23 | Pressure | Alarm | Standard | DPTH_4ComAlr |  | 1x0277 | 4.18 | BI251 | 4.18 | 0 | 1 |  | Communication Alarm DPTH4 | Kommunikation Alarm DPTH4 | Communication Alarm DPTH4
0x1F24 | Pressure | Alarm | Standard | DPTH_5ComAlr |  | 1x0278 | 4.18 | BI252 | 4.18 | 0 | 1 |  | Communication Alarm DPTH5 | Kommunikation Alarm DPTH5 | Communication Alarm DPTH5
0x1F27 | Filter | Alarm | Standard | SupFilt2AlrOn |  | 1x0279 | 4.18 | BI255 | 4.18 | 0 | 1 |  | Alarm from Supplyfilter2filtertimer | Alarm fra Tilluft filter2 - Timer for filterskift er overskredet | Alarm from Supplyfilter2filtertimer
0x1F28 | Filter | Alarm | Standard | ExtFilt2AlrOn |  | 1x0280 | 4.18 | BI256 | 4.18 | 0 | 1 |  | Alarm from Extractfilter2timer | Alarm fra Fraluft filter2 - Timer for filterskift er overskredet | Alarm from Extractfilter2timer
0x1ECE | Heating | Alarm | Standard | AlrFrostLuft |  | 1x0281 | 4.18 | BI83 | 4.18 | 0 | 1 |  | Alarm from frost thermostat | Alarm fra frosttermostat | Alarm frost thermostat alarm (digital input)
0x1998 | Fan, Supply drive 2 | Alarm | Special | EC2sup_ErrDir |  | 1x0282 | 4.18 | BI125 | 4.18 |  |  |  | EC2-SupplyMotor Direction error | EC2-Tilluftsmotor omdrejningsretning fejl | OJ-EC/-DV2-Supply air motor Direction error
0x19B8 | Fan, Extract drive 2 | Alarm | Special | EC2ext_ErrDir |  | 1x0283 | 4.18 | BI133 | 4.18 | 0 | 1 |  | EC-ExtractMotor Direction error | EC2-Fraluftsmotor omdrejningsretning fejl | OJ-EC/-DV-ExtractMotor Direction error
0x1EA4 | Fan, Supply drive 2 | Alarm | Special | AlrEC2SupCom |  | 1x0284 | 4.18 | BI135 | 4.18 | 0 | 1 |  | OJ-EC2 Supply Comm Alarm | OJ-EC2 Tilluft Fælles Alarm | OJ-EC/-DV2 Supply Comm Alarm
0x1EA5 | Fan, Extract drive 2 | Alarm | Special | AlrEC2ExtCom |  | 1x0285 | 4.18 | BI136 | 4.18 | 0 | 1 |  | OJ-EC2 Extract Comm Alarm | OJ-EC2 Fraluft Fælles Alarm | OJ-EC/-DV2 Extract Comm Alarm
0x1958 | Fan, Supply drive | Alarm | Standard | ECsup_ErrDir |  | 1x0286 | 4.18 | BI143 | 4.18 | 0 | 1 |  | EC-SupplyMotor Direction error | EC-Tilluftsmotor omdrejningsretning fejl | OJ-EC/-DV-SupplyMotor Direction error
0x1978 | Fan, Extract drive | Alarm | Standard | ECext_ErrDir |  | 1x0287 | 4.18 | BI151 | 4.18 | 0 | 1 |  | EC-ExtractMotor Direction error | EC-Fraluftsmotor omdrejningsretning fejl | OJ-EC/-DV-ExtractMotor Direction error
0x1E6C | Fan, Supply drive | Alarm | Standard | AlrOJ_ECS_Comm |  | 1x0288 | 4.18 | BI153 | 4.18 | 0 | 1 |  | OJ-EC Supply Comm Alarm | OJ-EC Tilluft Fælles Alarm | OJ-EC/-DV Supply Comm Alarm
0x1E6D | Fan, Extract drive | Alarm | Standard | AlrOJ_ECE_Comm |  | 1x0289 | 4.18 | BI154 | 4.18 | 0 | 1 |  | OJ-EC Extract Comm Alarm | OJ-EC Fraluft Comm Alarm | OJ-EC/-DV Extract Comm Alarm
0x1EF6 | Damper, Smoke evac. | Alarm | Special | AlrBDRes7Com |  | 1x0290 | 4.18 | BI156 | 4.18 | 0 | 1 |  | Communication Alarm Belimo ResNo7 Damper | KommunikationsAlarm Belimo ResNo7 Spjæld | Communication Alarm Belimo ResNo7 Damper
0x1E76 | Damper, Smoke evac. | Alarm | Special | AlrBDRes7Pos |  | 1x0291 | 4.18 | BI157 | 4.18 | 0 | 1 |  | Position Alarm Belimo ResNo7 Damper | PositionsAlarm Belimo ResNo7 Spjæld | Position Alarm Belimo ResNo7 Damper
0x1EA8 | Temp. sensor | Alarm | Special | AlrSupTemp2 |  | 1x0292 | 4.18 | BI166 | 4.18 | 0 | 1 |  | Supplysensor 2 alarm | Tilluftsføler 2 alarm | Supplysensor 2 alarm
0x1E56 | Fan, Supply drive | Alarm | Standard | AlrSupMtr |  | 1x0293 | 4.18 | BI171 | 4.18 | 0 | 1 |  | SupMotor Alarm | Tilluft Motor Alarm | SupMotor Alarm
0x1E57 | Fan, Extract drive | Alarm | Standard | AlrExtMtr |  | 1x0294 | 4.18 | BI172 | 4.18 | 0 | 1 |  | ExtMotor Alarm | Fraluft Motor Alarm | ExtMotor Alarm
0x1E98 | Fan, ATV drive | Alarm | Special | AlrAtvSupComm |  | 1x0295 | 4.18 | BI96 | 4.18 | 0 | 1 |  | Alarm Atv Comm Supply | Fælles Alarm Atv Tilluft | Alarm Atv Communication alarm Supply
0x1E99 | Fan, ATV drive | Alarm | Special | AlrAtvExtComm |  | 1x0296 | 4.18 | BI97 | 4.18 | 0 | 1 |  | Alarm Atv Comm Extract | Fælles Alarm Atv Fraluft | Alarm Atv Ccommunication alarm Extract
0x1E9A | Fan, ATV drive | Alarm | Special | AlrAtvSupFC |  | 1x0297 | 4.18 | BI98 | 4.18 | 0 | 1 |  | Alarm Atv FC Supply | Alarm Atv FC Tilluft | Alarm Atv FC Supply
0x1E9B | Fan, ATV drive | Alarm | Special | AlrAtvExtFC |  | 1x0298 | 4.18 | BI99 | 4.18 | 0 | 1 |  | Alarm Atv FC Extract | Alarm Atv FC Fraluft | Alarm Atv FC Extract
0x1E9D | Preheater coil, electric | Alarm | Special | AlrDeIceCont |  | 1x0299 | 4.18 | BI101 | 4.18 | 0 | 1 |  | Contact error DeIcer El-coil | Kontaktor fejl Afisning El-flade | Contact error DeIcer El-coil
0x1E9E | Preheater coil, electric | Alarm | Special | AlrDeIceOverh |  | 1x0300 | 4.18 | BI102 | 4.18 | 0 | 1 |  | DeIcer overheatingsalarm El-coil | Afisning overhedningsalarm El-flade | DeIcer overheatingsalarm El-coil
0x1E9F | Preheater coil, electric | Alarm | Special | AlrDeIceReduc |  | 1x0301 | 4.18 | BI103 | 4.18 | 0 | 1 |  | DeIcer power reduction alarm El-coil | Afisning effekt reduktion alarm El-flade | DeIcer power reduction alarm El-coil
0x1202 | Fan, Extract drive | Alarm | Standard | ExtMotorAlarm |  | 1x0302 | 4.18 | BI60 | 4.18 | 0 | 1 |  | ExtractMotor ON/OFF | Fraluftsmotor ON/OFF | ExtractMotor ON/OFF
| Zone, PIR | Status | Standard | ZM_PIR |  | 1x0303 | 4.19 | BI257 | 4.19 | 0 | 1 |  |  |  | ZoneControl PIR Active
| Zone 1 | Status | Standard | ZM1_WinFrost |  | 1x0304 | 4.19 | BI258 | 4.19 | 0 | 1 |  |  |  | ZoneModule 1 - WindowFrost Value
| Zone 1 | Status | Standard | ZM1_PIR |  | 1x0305 | 4.19 | BI259 | 4.19 | 0 | 1 |  |  |  | ZoneModule 1 - PIR Active
| Zone 1 | Status | Standard | ZM1_RoomTmpErr |  | 1x0306 | 4.19 | BI260 | 4.19 | 0 | 1 |  |  |  | ZoneModule 1 - Room Temp Sensor Error
| Zone 1 | Status | Standard | ZM1_SupTempErr |  | 1x0307 | 4.19 | BI261 | 4.19 | 0 | 1 |  |  |  | ZoneModule 1 - Supply Temp Sensor Error
| Zone 2 | Status | Standard | ZM2_WinFrost |  | 1x0308 | 4.19 | BI262 | 4.19 | 0 | 1 |  |  |  | ZoneModule 2 - WindowFrost Value
| Zone 2 | Status | Standard | ZM2_PIR |  | 1x0309 | 4.19 | BI263 | 4.19 | 0 | 1 |  |  |  | ZoneModule 2 - PIR Active
| Zone 2 | Status | Standard | ZM2_RoomTmpErr |  | 1x0310 | 4.19 | BI264 | 4.19 | 0 | 1 |  |  |  | ZoneModule 2 - Room Temp Sensor Error
| Zone 2 | Status | Standard | ZM2_SupTempErr |  | 1x0311 | 4.19 | BI265 | 4.19 | 0 | 1 |  |  |  | ZoneModule 2 - Supply Temp Sensor Error
| Zone 3 | Status | Standard | ZM3_WinFrost |  | 1x0312 | 4.19 | BI266 | 4.19 | 0 | 1 |  |  |  | ZoneModule 3 - WindowFrost Value
| Zone 3 | Status | Standard | ZM3_PIR |  | 1x0313 | 4.19 | BI267 | 4.19 | 0 | 1 |  |  |  | ZoneModule 3 - PIR Active
| Zone 3 | Status | Standard | ZM3_RoomTmpErr |  | 1x0314 | 4.19 | BI268 | 4.19 | 0 | 1 |  |  |  | ZoneModule 3 - Room Temp Sensor Error
| Zone 3 | Status | Standard | ZM3_SupTempErr |  | 1x0315 | 4.19 | BI269 | 4.19 | 0 | 1 |  |  |  | ZoneModule 3 - Supply Temp Sensor Error
| Zone 4 | Status | Standard | ZM4_WinFrost |  | 1x0316 | 4.19 | BI270 | 4.19 | 0 | 1 |  |  |  | ZoneModule 4 - WindowFrost Value
| Zone 4 | Status | Standard | ZM4_PIR |  | 1x0317 | 4.19 | BI271 | 4.19 | 0 | 1 |  |  |  | ZoneModule 4 - PIR Active
| Zone 4 | Status | Standard | ZM4_RoomTmpErr |  | 1x0318 | 4.19 | BI272 | 4.19 | 0 | 1 |  |  |  | ZoneModule 4 - Room Temp Sensor Error
| Zone 4 | Status | Standard | ZM4_SupTempErr |  | 1x0319 | 4.19 | BI273 | 4.19 | 0 | 1 |  |  |  | ZoneModule 4 - Supply Temp Sensor Error
| Cooling coil | Status | Standard | Cool_RE2 |  | 1x0320 | 4.22 | BI274 | 4.21 | 0 | 1 |  |  |  | Cooling Relay 2
| Cooling coil | Status | Standard | Cool_RE3 |  | 1x0321 | 4.22 | BI275 | 4.21 | 0 | 1 |  |  |  | Cooling Relay 3
| Cooling coil | Status | Standard | Cool_RE4 |  | 1x0322 | 4.22 | BI276 | 4.21 | 0 | 1 |  |  |  | Cooling Relay 4
| Fan Wall, Supply | Alarm | Standard | SupFanWallAlr |  | 1x0323 | 6.30 | BI286 | 6.30 | 0 | 1 |  |  |  | Supply Fan wall Alarm (B)
| Fan Wall, Exhaust | Alarm | Standard | ExtFanWallAlr |  | 1x0324 | 6.30 | BI287 | 6.30 | 0 | 1 |  |  |  | Extract Fan wall Alarm (B)
| Damper, Extract air | Status | Standard | ExtDamperSig |  | 1x0325 | 6.30 | BI288 | 6.30 | 0 | 1 |  |  |  | The extract digital damper output signal ("1" = Open damper)
| Damper, Exhaust | Status | Standard | ExhDamperSig |  | 1x0326 | 6.30 | BI289 | 6.30 | 0 | 1 |  |  |  | The exhaust digital damper output signal ("1" = Open damper)
| Damper, Backup Exhaust | Status | Standard | ExhBDamperSig |  | 1x0327 | 6.30 | BI290 | 6.30 | 0 | 1 |  |  |  | The exhaust backup digital damper output signal ("1" = Open damper)
| Damper, Backup Supply | Status | Standard | SupBDamperSig |  | 1x0328 | 6.30 | BI291 | 6.30 | 0 | 1 |  |  |  | The supply backup digital damper output signal ("1" = Open damper)
0x1B40 | Fan, supply | Status | Standard | AlrComSupFan |  | 1x0500 | x.xx | BI185 | x.xx | 0 | 1 |  | Common-Alarm Supplyfan | Fælles Alarm - tilluftventilator | Common Alarm - supply air fan
0x1B41 | Fan, supply | Alarm | Standard | AlrComSupFlDu |  | 1x0501 | x.xx | BI187 | x.xx | 0 | 1 |  | Common-Alarm Supply duct/flow | Fælles Alarm - tilluft tryk/flow | Common Alarm - supply pressure/flow
0x1B42 | Fan | Alarm | Standard | AlrComExtFan |  | 1x0502 | x.xx | BI186 | x.xx | 0 | 1 |  | Common-Alarm Extractfan | Fælles Alarm - Fraluftsventilator | Common Alarm - extract fan
0x1B43 | Fan | Alarm | Standard | AlrComExtFlDu |  | 1x0503 | x.xx | BI188 | x.xx | 0 | 1 |  | Common-Alarm Extract duct/flow | Fælles Alarm - Fraluft tryk/flow | Common Alarm - extract pressure/flow
0x1B44 | Heating coil, Water | Alarm | Standard | AlrComHWPump |  | 1x0504 | x.xx | BI184 | x.xx | 0 | 1 |  | Common-Alarm circulationpumps | Fælles Alarm - cirkulationspumpe | Common Alarm - circulation pump
0x1B45 | Heat exchanger | Alarm | Standard | AlrComEXC |  | 1x0505 | x.xx | BI189 | x.xx | 0 | 1 |  | Common-Alarm Exchanger | Fælles Alarm - varmeveksler | Common Alarm - heat exchanger
0x1B46 | Heating coil, Water | Alarm | Standard | AlrComFreeze |  | 1x0506 | x.xx | BI190 | x.xx | 0 | 1 |  | Common-Alarm antifreeze | Fælles Alarm - frost | Common Alarm - frost
0x1B47 | Heating coil, Electric | Alarm | Standard | AlrComElHeat |  | 1x0507 | x.xx | BI191 | x.xx | 0 | 1 |  | Common-Alarm El-Coils | Fælles Alarm - elflade | Common Alarm - electric heating coil
0x1B48 | AHU controller | Alarm | Standard | AlrComTemp |  | 1x0508 | x.xx | BI192 | x.xx | 0 | 1 |  | Common-Alarm Temperatures low/high | Fælles Alarm - temperatur høj/lav | Common Alarm - temperature high/low
0x1B49 | Filter | Alarm | Standard | AlrComSFilt |  | 1x0509 | x.xx | BI193 | x.xx | 0 | 1 |  | Common-Alarm Supply Filter | Fælles Alarm - tilluft filter | Common Alarm - supply filter
0x1B4A | Filter | Alarm | Standard | AlrComEFilt |  | 1x0510 | x.xx | BI194 | x.xx | 0 | 1 |  | Common-Alarm Extract Filter | Fælles Alarm - Fraluft filter | Common Alarm - extract filter
0x1B4B | Temp. sensor | Alarm | Standard | AlrComTmpSens |  | 1x0511 | x.xx | BI195 | x.xx | 0 | 1 |  | Common-Alarm Temperaturesensors | Fælles Alarm - temperaturføler | Common Alarm - temperature sensor
0x1B4C | Cooling coil | Alarm | Standard | AlrComCool |  | 1x0512 | x.xx | BI196 | x.xx | 0 | 1 |  | Common-Alarm Cooling | Fælles Alarm - køling | Common Alarm - cooling
0x1B4D | Damper, Direct Modbus | Alarm | Standard | AlrComBDamp |  | 1x0513 | x.xx | BI197 | x.xx | 0 | 1 |  | Common-Alarm Dampers Belimo | Fælles - Alarm Belimo spjæld | Common Alarm Belimo damper ("1" = Open damper)
0x1B4E | AHU controller | Alarm | Standard | AlrComIntern |  | 1x0514 | x.xx | BI198 | x.xx | 0 | 1 |  | Common-Alarm Internals / SysModBus | Fælles Alarm - intern Modbus fejl | Common Alarm - Internal Modbus error
0x112D | AHU controller | Status | Standard | BMS_InpStat |  | 1x0515 | 4.18 | BI199 | 4.18 | 0 | 1 |  | Activate BMS control | Aktivér BMS control | Activate BMS control
0x1019 | AHU controller | Status | Standard | ExternLowState |  | 1x0522 | x.xx | BI200 | x.xx | 0 | 1 |  | State of extern lowspeed input | Indgang ekstern lav hastighed | Input external low speed
0x101A | AHU controller | Status | Standard | StartInpState |  | 1x0523 | x.xx | BI177 | x.xx | 0 | 1 |  | State of extern start input | Status ekstern start indgang | Status external start input
| 1. Info | 1. Info | 1. Info | 1. Info |  | Input register (R) |  | Analog input (R) | 1. Info | 1. Info | 1. Info | 1. Info |  |  | 1. Info
0x2030 | AHU controller | Control | Standard | DriftMode |  | 3x0001 | x.xx | AI0 | x.xx | 0 | 500 |  | Current DriftMode 000-099:Agg Stop 100-199:Agg Lo Speed 200-299:Agg Hi Speed 300-399:Spec RegMode Agg Med Speed 410-414 | Aktuel Driftform 000-099:Anlæg Stop 100-199:Anlæg Lav Hastighed 200-299:Anlæg Høj Hastighed 300-399:Anlæg Spec RegMode 410-414:Anlæg Medium Hastighed | Actual operating mode 000-099: Unit stopped 100-199: Unit in low speed mode 200-299: Unit in high speed mode 300-399: Unit in spec. control mode 410-414: Unit in medium speed mode
0x2162 | Pressure | Current value | Standard | SupDuctPa | Pa | 3x0003 | x.xx | AI1 | x.xx | 0 | 5000 |  | Supply DuctPressure (Calc from PressSignal) [Pa] | Aktuel kanaltryk tilluft [Pa] | Actual supply duct pressure [Pa]
0x2163 | Pressure | Set point | Standard | SupDuctPaRgSet | Pa | 3x0004 | x.xx | AI2 | x.xx | 0 | 2000 |  | Regulator SetPoint for DuctPressReg [Pa] | Regulator setpunkt for kanal tryk regulator [Pa] | Setpoint for supply duct pressure controller [Pa]
0x2262 | Pressure | Current value | Standard | ExtDuctPa | Pa | 3x0005 | x.xx | AI3 | x.xx | 0 | 5000 |  | Extract DuctPressure (Calc from PressSignal) [Pa] | Aktuel kanaltryk fraluft [Pa] | Actual extract duct pressure [Pa]
0x2263 | Pressure | Set point | Standard | ExtDuctPaRgSet | Pa | 3x0006 | x.xx | AI4 | x.xx | 0 | 2000 |  | Regulator SetPoint for DuctPressReg [Pa] | Regulator setpunkt for kanaltryk regulering [Pa] | Setpoint for extract duct pressure controller [Pa]
0x2140 | Fan | Current value | Standard | SupFlow | l/s | 3x0007 | x.xx | AI5 | x.xx | 0 | 30000 |  | Current SupplyFlow [l/s] | Aktuel flow tilluft [l/s] | Actual supply flow [l/s] or [m3/h] or [CFM] (Depending on the unit selection in the OJ-Air2Master)
0x2141 | Fan | Set point | Standard | SupFlowRegSet | l/s | 3x0008 | x.xx | AI6 | x.xx | 0 | 30000 |  | Regulator SupplyFlow-Set [l/s] | Regulator tilluft flow-setpunkt [l/s] | Setpoint for supply flow controller [l/s] or [m3/h] or [CFM] (Depending on the unit selection in the OJ-Air2Master)
0x2240 | Fan | Current value | Standard | ExtFlow | l/s | 3x0009 | x.xx | AI7 | x.xx | 0 | 30000 |  | Current ExtractFlow [l/s] | Aktuel fraluft flow [l/s] | Actual extract flow [l/s] or [m3/h] or [CFM] (Depending on the unit selection in the OJ-Air2Master)
0x2241 | Fan | Set point | Standard | ExtFlowRegSet | l/s | 3x0010 | x.xx | AI8 | x.xx | 0 | 30000 |  | Regulator ExtractFlow-Set [l/s] | Regulator fraluft flow-setpunkt [l/s] | Setpoint for extract flow controller [l/s] or [m3/h] or [CFM] (Depending on the unit selection in the OJ-Air2Master)
0x2450 | CO2 sensor | Current value | Standard | CO2_ppmMeas | ppm | 3x0011 | x.xx | AI9 | x.xx | 0 | 10000 |  | CO2 Sensor ppm Measure [ppm] | CO2 føler ppm Måling [ppm] | CO2 concentration recorded by CO2 sensor [ppm]
0x2441 | Fan | Current value | Standard | MtrFanSupVin | % | 3x0012 | x.xx | AI10 | x.xx | 0 | 10000 |  | FAN-Optimize Signal [%] | 0-10VDC signal til tilluft motor | 0-10 V DC signal to supply motor
0x2442 | Fan | Current value | Standard | MtrFanExtVin | % | 3x0013 | x.xx | AI11 | x.xx | 0 | 10000 |  | 0-10VDC External Supply Motor Signal (FAN-Opt) | 0-10VDC signal til fraluft motor | 0-10 V DC signal to extract motor
0x2470 | Fan optimizer | Current value | Standard | FAN_SupPrcMeas | % | 3x0014 | x.xx | AI12 | x.xx | 0 | 10000 |  | FAN-Opt Supply Signal [1/100%] | Spænding på FAN-Optimizer indgang; tilluft sgnal [1/100%] | Voltage on fan optimizer input: supply signal [1/100%]
0x2471 | Fan optimizer | Current value | Standard | FAN_ExtPrcMeas | % | 3x0015 | x.xx | AI13 | x.xx | 0 | 10000 |  | FAN-Opt Extract Signal [1/100%] | Spænding på FAN-Optimizer indgang; fraluft signal [1/100%] | Voltage on fan optimizer input: extract signal [1/100%]
0x3141 | Fan | Set point | Standard | SupFC_MaxFlow | l/s | 3x0016 | x.xx | AI14 | x.xx | 100 | 30000 | 10000 | Supply FC-Max Flow [l/s] | tilluft FC-Max Flow [l/s] or [m3/h] or [CFM] (Depending on the unit selection in the OJ-Air2Master) | Supply FC max. flow [l/s] or [m3/h] or [CFM] (Depending on the unit selection in the OJ-Air2Master)
0x3241 | Fan | Set point | Standard | ExtFC_MaxFlow | l/s | 3x0017 | x.xx | AI15 | x.xx | 100 | 30000 | 10000 | Extract FC-Max Flow [l/s] | fraluft FC-Max Flow [l/s] or [m3/h] or [CFM] (Depending on the unit selection in the OJ-Air2Master) | Extract FC max. flow [l/s] or [m3/h] or [CFM] (Depending on the unit selection in the OJ-Air2Master)
0x2100 | Temp. Supply | Current value | Standard | SupTemp | °C | 3x0020 | x.xx | AI16 | x.xx | -4000 | 10000 |  | Current SupplyTemp [1/100°C] | Aktuel tilluftstemperatur [1/100°C] | Actual supply temperature [1/100°C]
0x2101 | Temp. Supply | Set point | Standard | SupTempRegSet | °C | 3x0021 | x.xx | AI17 | x.xx | 0 | 4000 |  | Regulator SupplyTemp-Set [1/100°C] | Regulator tillufttemperatur-Setpunkt [1/100°C] | Setpoint for supply temperature controller [1/100°C]
0x2200 | Temp. Extract | Current value | Standard | ExtTemp | °C | 3x0022 | x.xx | AI18 | x.xx | -4000 | 10000 |  | Current ExtractTemp [1/100°C] | Aktuel fraluft temperatur [1/100°C] | Actual extract temperature [1/100°C]
0x2201 | Temp. Extract | Set point | Standard | ExtTempRegSet | °C | 3x0023 | x.xx | AI19 | x.xx | 10 | 4000 |  | Regulator ExtractTemp-Set [1/100°C] | Regulator fralufttemp-setpunkt [1/100°C] | Setpoint for extract temperature controller [1/100°C]
0x2300 | Temp. out door | Current value | Standard | OutDoorTemp | °C | 3x0024 | x.xx | AI20 | x.xx | -6000 | 10000 |  | Current OutDoorTemp [1/100°C] | Aktuel ude temperatur [1/100°C] | Actual outdoor temperature [1/100°C] OBS! Only valid when no external outdoor sensor configured - alternative use AI233 (3x0024)
0x2310 | Temp. room | Current value | Standard | RoomTemp | °C | 3x0025 | x.xx | AI21 | x.xx | -4000 | 10000 |  | Current RoomTemp (External Sens) [1/100C] | Aktuel rum temperatur [1/100°C] | Actual room temperature [1/100°C]
0x2320 | Temp. Exhaust | Current value | Standard | ExhaustTemp | °C | 3x0026 | x.xx | AI22 | x.xx | -4000 | 10000 |  | Current ExhaustTemp [1/100°C] | Aktuel afkast [1/100°C] | Actual exhaust temperature [1/100°C]
0x2460 | AHU controller | Current value | Standard | TempRegMeas | °C | 3x0027 | x.xx | AI23 | x.xx | -4000 | 10000 |  | TempMeas for actual RegMode [1/100°C] | Temp. måling for aktuel reguleringsvalg [1/100°C] | Temp. recorded by actual temperature controller [1/100°C]
0x2461 | AHU controller | Set point | Standard | TempRegVal | °C | 3x0028 | x.xx | AI24 | x.xx | 0 | 4000 |  | RegVal for actual RegMode [1/100C] | Reguleringsværdi for aktuel reguleringsvalg [1/100°C] | Control value for actual temperature controller [1/100°C]
0x2920 | Temp. after heat recovery | Current value | Standard | BattEXC_Temp | °C | 3x0029 | x.xx | AI25 | x.xx | -4000 | 10000 |  | WaterCoil Temp after EXC [1/100°C] | Vandflade temperatur efter varmeveksler [1/100°C] | Water coil temperature downstream from heat exchanger [1/100°C]
0x2330 | Heating coil 1, Water | Current value | Standard | HW1BattTemp | °C | 3x0030 | x.xx | AI26 | x.xx | -4000 | 10000 |  | Current HeatWaterCoilTemp [1/100°C] | Aktuel varmeflade temperatur [1/100°C] | Actual heating coil temperature [1/100°C]
0x2121 | Filter | Current value | Standard | SupFiltPaAvr | Pa | 3x0031 | x.xx | AI27 | x.xx | 0 | 5000 |  | Supply FilterPressure (Avr-Meas) [Pa] | tilluft filtertryk [Pa] | Supply filter pressure [Pa]
0x2221 | Filter | Current value | Standard | ExtFiltPaAvr | Pa | 3x0032 | x.xx | AI28 | x.xx | 0 | 5000 |  | Extract FilterPressure (Avr-Meas) [Pa] | fraluft filtertryk [Pa] | Extract filter pressure [Pa]
0x239A | Filter | Average value | Standard | FiltSupFlowAvr | Pa | 3x0033 | x.xx | AI266 | 6.41 | 0 | 2000 |  | Average supflow-pressure [Pa] DYNAMICMODE ONLY (zero in staticmode) | Gennemsnit filter tilluftflow - anvendes internt ved dynamisk filterudmåling [Pa] | Average filter supply flow - for internal use only in connection to dynamic filter suveilance [Pa]
0x2160 | Fan | Set point | Standard | SupMotorSet | % | 3x0034 | x.xx | AI29 | x.xx | 0 | 10000 |  | Supply MotorSignal [%] | tilluft motorsignal setpunkt [%] | supply motor signal setpoint [1/100%]
0x239B | Filter | Average value | Standard | FiltExtFlowAvr | Pa | 3x0035 | x.xx | AI267 | 6.41 | 0 | 2000 |  | Average extflow-pressure [Pa] DYNAMICMODE ONLY (zero in staticmode) | Gennemsnit filter fraluftflow - anvendes internt ved dynamisk filterudmåling [Pa] | Average filter exhaust flow - for internal use only in connection to dynamic filter suveilance [Pa]
0x2260 | Fan | Set point | Standard | ExtMotorSet | % | 3x0036 | x.xx | AI30 | x.xx | 0 | 10000 |  | Extract MotorSignal [%] | fraluft motorsignal setpunkt [%] | Extract motor signal setpoint [%]
0x239C | Filter | Average value | Standard | FiltSupPaAvr | Pa | 3x0037 | x.xx | AI268 | 6.41 | 0 | 3000 |  | Average supfilter-pressure [Pa/30] DYNAMICMODE ONLY (zero in staticmode) | Gennemsnit af de sidste 30 målinger trykfald filter tilluft [Pa/30] | Average supfilter-pressure [Pa/30]
0x239D | Filter | Average value | Standard | FiltExtPaAvr | Pa | 3x0038 | x.xx | AI269 | 6.41 | 0 | 3000 |  | Average extfilter-pressure [Pa/30] DYNAMICMODE ONLY (zero in staticmode) | Gennemsnit af de sidste 30 målinger trykfald filter fraluft [Pa/30] | Average extfilter-pressure [Pa/30]
0x2394 | Filter | Set point | Standard | FiltSupAlrPa | Pa | 3x0039 | x.xx | AI31 | x.xx | 0 | 100 |  | Filter pressure for alarm-limit at actual flow [Pa] DYNAMICMODE ONLY (zero in staticmode) | tilluft filterovervågning max. alarm-grænse[Pa] KUN DYNAMICMODE ("0" er STATICMODE) | supply filter monitor max. alarm limit [Pa] ONLY IN DYNAMIC MODE ("0" IS STATIC MODE)
0x2395 | Filter | Set point | Standard | EfficiencyTemp | Pa | 3x0040 | 5.07 | AI232 | 5.07 | 0 | 100 |  | Filter pressure for alarm-limit at actual flow [Pa] DYNAMICMODE ONLY (zero in staticmode) | fraluft. filterovervågning max. alarm-grænse [Pa] KUN DYNAMICMODE ("0" er STATICMODE) | Current EfficiencyTemp [1/100C]
0x236C | Temp. heat pump | Current value | Special | HP_OutdCoilTmp | °C | 3x0041 | x.xx | AI270 | 6.41 | -6000 | 10000 |  | Current air temperature just before the outdoor coil of the heat pump [1/100°C] | Aktuel udetemperatur ved varmepumpens udedel [1/100°C] | Actual outdoor temperature near outdoor heat pump parts [1/100°C]
0x2A84 | Heat exchanger | Current value | Standard | EXCActualEff | % | 3x0042 | x.xx | AI108 | x.xx | 0 | 10000 |  | EXC actual Efficiency in [1/100%] | Varmeveksler virkningsgrad [1/100%] | Heat exchanger efficiency [1/100%]
0x2AF4 | Fan, ATV drive | Alarm | Special | AtvSupFCType |  | 3x0043 | x.xx | AI106 | x.xx | 0 | 30000 |  | SupplyMotor Actual Alarmstatus | tilluft ATV frekvensomformer; Aktuel FC Type | Supply ATV frequency converter - Actual FC type
0x2AFC | Fan, ATV drive | Alarm | Special | AtvExtFCType |  | 3x0044 | x.xx | AI107 | x.xx | 0 | 30000 |  | ExtractMotor Actual Alarmstatus | fraluft ATV frekvensomformer; Aktuel FC Type | Exhaust ATV frequency converter - Actual FC type
0x239E | Filter | Set point | Standard | FiltSup2AlrPa | Pa | 3x0045 | 4.18 | AI271 | 6.41 | 0 | 100 |  | Supply Filter2 pressure for alarm-limit at actual flow [Pa] DYNAMICMODE ONLY ("0" in staticmode) | Tilluft Beregnet alarm for dynamisk filterovervågning ved aktuel volume [Pa] KUN VED DYNAMISK OVERVÅGNING ("0" in staticmode) | Filter pressure for alarm-limit at actual flow [Pa] DYNAMICMODE ONLY (zero in staticmode)
0x239F | Filter | Set point | Standard | FiltExt2AlrPa | Pa | 3x0046 | 4.18 | AI272 | 6.41 | 0 | 100 |  | Extract Filter2 pressure for alarm-limit at actual flow [Pa] DYNAMICMODE ONLY ("0" in staticmode) | Fraluft Beregnet alarm for dynamisk filterovervågning ved aktuel volume [Pa] KUN VED DYNAMISK OVERVÅGNING ("0" in staticmode) | Filter pressure for alarm-limit at actual flow [Pa] DYNAMICMODE ONLY (zero in staticmode)
0x2125 | Filter | Average value | Standard | ExtFilt2PaAvr | Pa | 3x0047 | 4.18 | AI130 | 4.18 | 0 | 5000 |  | Supply FilterPressure (Avr-Meas) [Pa] | Tilluft 2 FlowTryk (Gsn-Måling) [Pa] | Extract 2 FlowPressure (Avr-Meas) [Pa]
|  |  | Standard | FiltExtAlrPa | Pa | 3x0048 | 5.07 | AI32 | 5.07 | 0 | 100 |  |  |  | Extract filter monitor max. alarm limit [Pa] ONLY IN DYNAMIC MODE ("0" IS STATIC MODE)
0x2126 | Filter | Average value | Standard | SupFilt2PaAvr | Pa | 3x0049 | 4.18 | AI131 | 4.18 | 0 | 5000 |  | Extract FilterPressure (Avr-Meas) [Pa] | Fraluft 2 FilterTryk (Gns-Måling) [Pa] | Supply 2 FilterPressure (Avr-Meas) [Pa]
0x23C0 | AHU controller | Set point | Standard | FlwTmpCmpOut | % | 3x0050 | x.xx | AI33 | x.xx | 0 | 10000 |  | FlowOutTempComp PercentOut [1/100°C] | Temp. korrigeret flow setpunkt procent [1/100°C] | Temp. compensated flow setpoint percentage [1/100%]
0x2380 | AHU controller | Summer/Winter comp. | Standard | SWTC_ActSetOfs | C | 3x0051 | x.xx | AI34 | x.xx | -1000 | 1000 |  | Sum/Wint-TempComp actual Setpoint offset [1/100°C] | Sommer/Vinter-Temp. kompensering på aktuel Setpunkt offset [1/100°C] | Summer/winter temp. compensation of actual setpoint offset [1/100°C]
0x2370 | AHU controller | Summer Night Cooling | Standard | SN_HeatTime | Sec | 3x0052 | x.xx | AI273 | 6.41 | 0 | 30000 |  | SummerNight Time whit Heat Demand [sec] | Aktuel tid med varmebehov indenfor sidste driftperiode (Sommernatkøling) [sec] | SummerNight Time with Heat Demand [sec]
0x2400 | Heat exchanger | Set point | Standard | HeatEXCPower | % | 3x0053 | x.xx | AI35 | x.xx | 0 | 10000 |  | EXC-Regulator HeatPower [1/100 %] | Varmeveksler-regulator varmeEffekt [1/100 %] | Heat exchange controller heating power [1/100%]
0x2401 | Heating | Set point | Standard | HeatPower | % | 3x0054 | x.xx | AI36 | x.xx | 0 | 10000 |  | AfterHeat-Regulator Power [1/100 %] | Aktuel varme-effekt [1/100 %] | Actual heating power [1/100%]
0x2420 | Cooling coil | Set point | Standard | CoolPower | % | 3x0055 | x.xx | AI37 | x.xx | 0 | 10000 |  | Cool Regulator Power [1/100 %] | Køling regulator effekt [1/100 %] | Cooling controller power [1/100%]
0x242A | Cooling coil | Set point | Standard | CoolActPower | % | 3x0056 | x.xx | AI38 | x.xx | 0 | 10000 |  | Actual Cool-Power [1/100%] | Aktuel køling-effekt [1/100%] | Actual cooling power [1/100%]
0x2421 | Cooling coil | Set point | Standard | CoolFlwForcePw | % | 3x0057 | x.xx | AI39 | x.xx | 0 | 10000 |  | Cool Force Flow Power [1/100 %] | Køle forcering flow effekt [1/100 %] | Cooling forced flow power [1/100%]
0x2426 | Cooling, DX | Current value | Standard | CoolVin1Alarm | % | 3x0058 | x.xx | AI40 | x.xx | 0 | 10000 |  | Cool Alarm-1 VDC-Signal [1/100 %] | Køle Alarm-1 Transducersignal [1/100 %] | Cooling alarm 1 transducer signal [1/100%]
0x2427 | Cooling, DX | Current value | Standard | CoolVin2Alarm | % | 3x0059 | x.xx | AI41 | x.xx | 0 | 10000 |  | Cool Alarm-2 VDC-Signal [1/100 %] | Køle Alarm-2 Transducersignal [1/100 %] | Cooling alarm 2 transducer signal [1/100%]
0x2428 | Cooling, DX | Current value | Standard | CoolVin3Alarm | % | 3x0060 | x.xx | AI42 | x.xx | 0 | 10000 |  | Cool Alarm-3 VDC-Signal [1/100 %] | Køle Alarm-3 Transducersignal [1/100 %] | Cooling alarm 3 transducer signal [1/100%]
0x2429 | Cooling, DX | Current value | Standard | CoolVin4Alarm | % | 3x0061 | x.xx | AI43 | x.xx | 0 | 10000 |  | Cool Alarm-4 VDC-Signal [1/100 %] | Køle Alarm-4 Transducersignal [1/100 %] | Cooling alarm 4 transducer signal [1/100%]
0x2500 | Cooling, DX | Current value | Standard | C_LoPress1Bar | Bar | 3x0062 | x.xx | AI44 | x.xx | 0 | 10000 |  | Actual LoPressSens-1 Bar [1/100 Bar] | Aktuel LavTrykFøler-1 Bar [1/100 Bar] | Actual low pressure sensor 1 [1/100 bar]
0x2501 | Cooling, DX | Current value | Standard | C_HiPress1Bar | Bar | 3x0063 | x.xx | AI45 | x.xx | 0 | 10000 |  | Actual HiPressSens-1 Bar [1/100 Bar] | Aktuel HøjTrykFøler-1 Bar [1/100 Bar] | Actual high pressure sensor 1 [1/100 bar]
0x2502 | Cooling, DX | Current value | Standard | C_LoPress2Bar | Bar | 3x0064 | x.xx | AI46 | x.xx | 0 | 10000 |  | Actual LoPressSens-2 Bar [1/100 Bar] | Aktuel LavTrykFøler-2 Bar [1/100 Bar] | Actual low pressure sensor 2 [1/100 bar]
0x2503 | Cooling, DX | Current value | Standard | C_HiPress2Bar | Bar | 3x0065 | x.xx | AI47 | x.xx | 0 | 10000 |  | Actual HiPressSens-2 Bar [1/100 Bar] | Aktuel HøjTrykFøler-2 Bar [1/100 Bar] | Actual high pressure sensor 2 [1/100 bar]
0x2408 | Heater coil 2 | Set point | Standard | Heat2Power | % | 3x0066 | x.xx | AI103 | x.xx | 0 | 10000 |  | AfterHeat2-Regulator Power [1/100 %] | Varme 2-Regulator Power [1/100 %] | Heating 2 - Regulator power [1/100%]
0x2A30 | Fan, Supply drive | Current value | Standard | FCsupMtrType |  | 3x0070 | x.xx | AI48 | x.xx | 0 | 256 |  | SupplyMotor Type | tilluftmotor Type (kun OJ-FC) | Supply motor type (only with OJ-FC)
0x2A31 | Fan, Supply drive | SW version | Standard | FCsupMtrFC_SW |  | 3x0071 | x.xx | AI49 | x.xx | 0 | 1000 |  | SupplyMotor Software Ver [1/100] | tilluftmotor software vers. [1/100] (kun OJ-FC) | Supply motor software version [1/100] (only with OJ-FC)
0x2A32 | Fan, Supply drive | SW version | Standard | FCsupMtrIO_SW |  | 3x0072 | x.xx | AI50 | x.xx | 0 | 1000 |  | SupplyMotor IO-Card Software Ver [1/100] | tilluftmotor IO-Kort Software Ver [1/100] (kun OJ-FC) | Supply motor IO card software version [1/100] (only with OJ-FC)
0x2A33 | Fan, Supply drive | Current value | Standard | FCsupMtrPrcOut | % | 3x0073 | x.xx | AI51 | x.xx | 0 | 10000 |  | SupplyMotor Percent Output [1/100%] | tilluftmotor procent udgang [1/100%] (kun OJ-FC) | Supply motor output percentage [1/100%] (only with OJ-FC)
0x2A34 | Fan, Supply drive | Current value | Standard | FCsupMtrHzOut | Hz | 3x0074 | x.xx | AI52 | x.xx | 0 | 10000 |  | SupplyMotor Frequency Output [1/100 Hz] | tilluftmotor frekvens udgang [1/100 Hz] (kun OJ-FC) | Supply motor frequency output [1/100 Hz] (only with OJ-FC)
0x2A37 | Fan, Supply drive | Current value | Standard | FCsupMtrIout | mA | 3x0075 | x.xx | AI53 | x.xx | 0 | 30000 |  | SupplyMotor Output Current [mA] | tilluftmotor aktuel strømudgang [mA] (kun OJ-FC) | Supply motor actual current output [mA] (only with OJ-FC)
0x2A38 | Fan, Supply drive | Current value | Standard | FCsupMtrPowOut | W | 3x0076 | x.xx | AI54 | x.xx | 0 | 6000 |  | SupplyMotor Output Power [Watt] | tilluftmotor aktuel effekt udgang [1/100 kWatt] (kun OJ-FC) | Supply motor actual power output [Watt] (only with OJ-FC)
0x2A3A | Fan, Supply drive | Set point | Standard | FCsupMtrPrcSet | % | 3x0077 | x.xx | AI55 | x.xx | 0 | 10000 |  | SupplyMotor Output Set [%] | tilluftmotor setpunkt [%] | Supply motor setpoint [%]
0x2143 | Fan, Supply drive | Current value | Standard | SupSFP | J/m | 3x0078 | x.xx | AI56 | x.xx | 0 | 10000 |  | Supply SFP [Ws/m3 same ase J/m3] | tilluft specific fan power (SFP) [Ws/m3 = J/m3] (kun OJ-FC) | Specific fan power (SFP), supply [W·s/m3 = J/m3] (only with OJ-FC)
|  |  | Standard | SupSFPII | J/m | 3x0079 | 5.07 | AI251 | 5.07 | 0 | 10000 |  |  |  | Supply SFP EC-2 [Ws/m3 same as J/m3]
0x2A50 | Fan, Extract drive | Current value | Standard | FCextMtrType |  | 3x0080 | x.xx | AI57 | x.xx | 0 | 256 |  | ExtractMotor Type | fraluftmotor type (kun OJ-FC) | Extract motor type (only with OJ-FC)
0x2A51 | Fan, Extract drive | SW version | Standard | FCextMtrFC_SW |  | 3x0081 | x.xx | AI58 | x.xx | 0 | 1000 |  | ExtractMotor Software Ver [1/100] | fraluftmotor software vers. [1/100] (kun OJ-FC) | Extract motor software version [1/100] (only with OJ-FC)
0x2A52 | Fan, Extract drive | SW version | Standard | FCextMtrIO_SW |  | 3x0082 | x.xx | AI59 | x.xx | 0 | 1000 |  | ExtractMotor IO-Card Software Ver [1/100] | fraluftmotor IO-Card Software Ver [1/100] (kun OJ-FC) | Extract motor IO card software version [1/100] (only with OJ-FC)
0x2A53 | Fan, Extract drive | Current value | Standard | FCextMtrPrcOut | % | 3x0083 | x.xx | AI60 | x.xx | 0 | 10000 |  | ExtractMotor Percent Output [1/100%] | fraluftmotor procent udgang [1/100%] (kun OJ-FC) | Extract motor output percentage [1/100%] (only with OJ-FC)
0x2A54 | Fan, Extract drive | Current value | Standard | FCextMtrHzOut | Hz | 3x0084 | x.xx | AI61 | x.xx | 0 | 10000 |  | ExtractMotor Frequency Output [1/100 Hz] | fraluftmotor frekvens udgang [1/100 Hz] (kun OJ-FC) | Extract motor frequency output [1/100 Hz] (only with OJ-FC)
0x2A57 | Fan, Extract drive | Current value | Standard | FCextMtrIout | mA | 3x0085 | x.xx | AI62 | x.xx | 0 | 30000 |  | ExtractMotor Output Current [mA] | fraluftmotor udgang aktuel strøm [mA] (kun OJ-FC) | Extract motor actual current output [mA] (only with OJ-FC)
0x2A58 | Fan, Extract drive | Current value | Standard | FCextMtrPowOut | W | 3x0086 | x.xx | AI63 | x.xx | 0 | 6000 |  | ExtractMotor Output Power [Watt] | fraluftmotor aktuel effekt udgang [1/100 kWatt] (kun OJ-FC) | Extract motor actual power output [Watt] (only with OJ-FC)
0x2A5A | Fan, Extract drive | Set point | Standard | FCextMtrPrcSet | % | 3x0087 | x.xx | AI64 | x.xx | 0 | 10000 |  | ExtractMotor Output Set [%] | fraluftmotor udgang setpunkt [%] | Extract motor output setpoint [1/100%]
0x2243 | Fan, Extract drive | Current value | Standard | ExtSFP | J/m | 3x0088 | x.xx | AI65 | x.xx | 0 | 10000 |  | Extract SFP [Ws/m3 same ase J/m3] | fraluft specific fan power (SFP) [Ws/m3 = J/m3] (kun OJ-FC) | Specific fan power (SFP), extract [W·s/m3 = J/m3] (only with OJ-FC)
|  |  | Standard | ExtSFPII | J/m | 3x0089 | 5.07 | AI252 | 5.07 | 0 | 10000 |  |  |  | Extract SFP EC-2 [Ws/m3 same as J/m3]
0x2A70 | Heat exchanger drive | Current value | Standard | EXC_Type |  | 3x0090 | x.xx | AI66 | x.xx | 0 | 3 |  | EXC-MotorType | Roterende varmeveksler - motortype (kun OJ RHX2M) | Rotary heat exchanger – motor type (only with OJ RHX2M)
0x2A71 | Heat exchanger drive | SW version | Standard | EXC_Software |  | 3x0091 | x.xx | AI67 | x.xx | 0 | 10000 |  | EXC-Software Ver [1/100] | Roterende varmeveksler - software vers. [1/100] (kun OJ RHX2M) | Rotary heat exchanger – software version [1/100] (only with OJ RHX2M)
0x2A72 | Heat exchanger drive | Current value | Standard | EXC_PrcOut | % | 3x0092 | x.xx | AI68 | x.xx | 0 | 10000 |  | EXC-Percent Out [1/100%] | Roterende varmeveksler-procent [1/100%] | Rotary heat exchanger – percentage [1/100%]
0x2A74 | Heat exchanger drive | Current value | Standard | EXC_RpmOut | rpm | 3x0093 | x.xx | AI69 | x.xx | 0 | 20000 |  | EXC-RpmOutput [1/100rpm] | Roterende varmeveksler-Omdr./min. udgang [1/100rpm] | Rotary heat exchanger – speed output [1/100 rpm]
0x2A76 | Heat exchanger drive | Current value | Standard | EXC_Iout | mA | 3x0094 | x.xx | AI70 | x.xx | 0 | 10000 |  | EXC-Current Out [mA] | Roterende varmeveksler-aktuel udgang [mA] (kun OJ RHX2M) | Rotary heat exchanger – actual output [mA] (only with OJ RHX2M)
0x2A77 | Heat exchanger drive | Current value | Standard | EXC_Power | W | 3x0095 | x.xx | AI71 | x.xx | 0 | 100 |  | EXC-Output Power [W] | Roterende varmeveksler-udgang effekt [W] (kun OJ RHX2M) | Rotary heat exchanger – output power [W] (only with OJ RHX2M)
0x2A79 | Heat exchanger drive | Current value | Standard | EXC_DriftDays | Day | 3x0096 | x.xx | AI72 | x.xx | 0 | 32000 |  | EXC-DriftDays | Roterende varmeveksler - antal driftdage (kun OJ RHX2M) | Rotary heat exchanger – days of operation (only with OJ RHX2M)
0x2A7A | Heat exchanger drive | Set point | Standard | EXC_PrcSet | % | 3x0097 | x.xx | AI73 | x.xx | 0 | 10000 |  | EXC-PercentSet [1/100%] | Roterende varmeveksler procent setpunkt [1/100%] (kun OJ RHX2M) | Rotary heat exchanger – percentage setpoint [1/100%] (only with OJ RHX2M)
|  |  | Standard | FullSFPHigh | J/m | 3x0098 | 5.07 | AI253 | 5.07 | 0 | 10000 |  |  |  | Combined SFP [Ws/m3 same as J/m3]
|  |  | Standard | FullSFPLow | J/m | 3x0099 | 5.07 | AI254 | 5.07 | 0 | 10000 |  |  |  | Combined SFP [Ws/m3 same as J/m3]
0x2A90 | IO Extension module | SW version | Standard | EXTM1_SW_Ver |  | 3x0100 | x.xx | AI74 | x.xx | 0 | 10000 |  | ExtensionModul-1 SoftwareVer [1/100] | ExtensionModul-1 SoftwareVer [1/100] | Extension module 1 software version [1/100]
0x2AB0 | IO Extension module | SW version | Standard | EXTM2_SW_Ver |  | 3x0101 | x.xx | AI75 | x.xx | 0 | 10000 |  | ExtensionModul-2 SoftwareVer [1/100] | ExtensionModul-2 SoftwareVer [1/100] | Extension module 2 software version [1/100]
0x2411 | Preheater coil | Current value | Standard | PHWMTemp | °C | 3x0102 | x.xx | AI105 | x.xx | -4000 | 10000 |  | Current HeatWaterCoilTemp [1/100°C] | Aktuel temperatur på forvarmeflade [1/100°C] | Actual temperature of pre-heating coil [1/100°C]
0x2413 | Preheater coil | Set point | Standard | PH_HeatPower | % | 3x0103 | x.xx | AI104 | x.xx | 0 | 10000 |  | Heatpower Preheater | Aktuel effekt på forvarmeflade [1/100%] | Actual output of pre-heating coil [1/100%]
0x2800 | AHU controller | Time | Standard | TimeSw-WeekDay |  | 3x0110 | x.xx | AI76 | x.xx | 0 | 6 |  | Current WeekDay (0-Mon..6-Sun) | Aktuel Ugedag (0-Man..6-Søn) | Actual day of the week (0=Mon..6=Sun)
0x2808 | AHU controller | Status | Standard | ExtDrfDaysLeft |  | 3x0111 | x.xx | AI77 | x.xx | 0 | 6 |  | Extended Drift Day's Left | Forlænget drift resterende antal dage | Extended operation, remaining number of days
0x2809 | AHU controller | Status | Standard | ExtDrfMinLeft | Min | 3x0112 | x.xx | AI78 | x.xx | 0 | 1439 |  | Extended Drift Minute's Left | Forlænget drift resterende antal minutter | Extended operation, remaining number of minutes
| Heat pump | Status | Special | HP_ExtAirTemp | °C | 3x0113 | 6.51 | AI338 | 6.51 | -5000 | 10000 |  |  |  | Actual temperature extract air after HeatPump [1/100°C]
0x236E | Heat pump | Current value | Special | HP_CoilPaMeas | Pa | 3x0115 | x.xx | AI110 | x.xx | 0 | 5000 |  | Actual pressure at the heat pump outdoor coil. | Aktuelt tryk ved varmepumpe udedel | Actual pressure at the heat pump outdoor coil.
0x2E10 | AHU controller | Alarm | Standard | Alr_Released00 |  | 3x0120 | x.xx | AI79 | x.xx | 0 | 100 |  | Stack for active alarm's (0 indicate end of stack) | Stack for aktive alarmer (0 indikerer slutningen af stack) | Stack for active alarms (0 indicates end of stack)
0x2E11 | AHU controller | Alarm | Standard | Alr_Released01 |  | 3x0121 | x.xx | AI80 | x.xx | 0 | 100 |  | Stack for active alarm's (0 indicate end of stack) | Stack for aktive alarmer (0 indikerer slutningen af stack) | Stack for active alarms (0 indicates end of stack)
0x2E12 | AHU controller | Alarm | Standard | Alr_Released02 |  | 3x0122 | x.xx | AI81 | x.xx | 0 | 100 |  | Stack for active alarm's (0 indicate end of stack) | Stack for aktive alarmer (0 indikerer slutningen af stack) | Stack for active alarms (0 indicates end of stack)
0x2E13 | AHU controller | Alarm | Standard | Alr_Released03 |  | 3x0123 | x.xx | AI82 | x.xx | 0 | 100 |  | Stack for active alarm's (0 indicate end of stack) | Stack for aktive alarmer (0 indikerer slutningen af stack) | Stack for active alarms (0 indicates end of stack)
0x2E14 | AHU controller | Alarm | Standard | Alr_Released04 |  | 3x0124 | x.xx | AI83 | x.xx | 0 | 100 |  | Stack for active alarm's (0 indicate end of stack) | Stack for aktive alarmer (0 indikerer slutningen af stack) | Stack for active alarms (0 indicates end of stack)
0x2E15 | AHU controller | Alarm | Standard | Alr_Released05 |  | 3x0125 | x.xx | AI84 | x.xx | 0 | 100 |  | Stack for active alarm's (0 indicate end of stack) | Stack for aktive alarmer (0 indikerer slutningen af stack) | Stack for active alarms (0 indicates end of stack)
0x2E16 | AHU controller | Alarm | Standard | Alr_Released06 |  | 3x0126 | x.xx | AI85 | x.xx | 0 | 100 |  | Stack for active alarm's (0 indicate end of stack) | Stack for aktive alarmer (0 indikerer slutningen af stack) | Stack for active alarms (0 indicates end of stack)
0x2E17 | AHU controller | Alarm | Standard | Alr_Released07 |  | 3x0127 | x.xx | AI86 | x.xx | 0 | 100 |  | Stack for active alarm's (0 indicate end of stack) | Stack for aktive alarmer (0 indikerer slutningen af stack) | Stack for active alarms (0 indicates end of stack)
0x2E18 | AHU controller | Alarm | Standard | Alr_Released08 |  | 3x0128 | x.xx | AI87 | x.xx | 0 | 100 |  | Stack for active alarm's (0 indicate end of stack) | Stack for aktive alarmer (0 indikerer slutningen af stack) | Stack for active alarms (0 indicates end of stack)
0x2E19 | AHU controller | Alarm | Standard | Alr_Released09 |  | 3x0129 | x.xx | AI88 | x.xx | 0 | 100 |  | Stack for active alarm's (0 indicate end of stack) | Stack for aktive alarmer (0 indikerer slutningen af stack) | Stack for active alarms (0 indicates end of stack)
0x2E1A | AHU controller | Alarm | Standard | Alr_Released10 |  | 3x0130 | x.xx | AI89 | x.xx | 0 | 100 |  | Stack for active alarm's (0 indicate end of stack) | Stack for aktive alarmer (0 indikerer slutningen af stack) | Stack for active alarms (0 indicates end of stack)
0x2E1B | AHU controller | Alarm | Standard | Alr_Released11 |  | 3x0131 | x.xx | AI90 | x.xx | 0 | 100 |  | Stack for active alarm's (0 indicate end of stack) | Stack for aktive alarmer (0 indikerer slutningen af stack) | Stack for active alarms (0 indicates end of stack)
0x2E1C | AHU controller | Alarm | Standard | Alr_Released12 |  | 3x0132 | x.xx | AI91 | x.xx | 0 | 100 |  | Stack for active alarm's (0 indicate end of stack) | Stack for aktive alarmer (0 indikerer slutningen af stack) | Stack for active alarms (0 indicates end of stack)
0x2E1D | AHU controller | Alarm | Standard | Alr_Released13 |  | 3x0133 | x.xx | AI92 | x.xx | 0 | 100 |  | Stack for active alarm's (0 indicate end of stack) | Stack for aktive alarmer (0 indikerer slutningen af stack) | Stack for active alarms (0 indicates end of stack)
0x2E1E | AHU controller | Alarm | Standard | Alr_Released14 |  | 3x0134 | x.xx | AI93 | x.xx | 0 | 100 |  | Stack for active alarm's (0 indicate end of stack) | Stack for aktive alarmer (0 indikerer slutningen af stack) | Stack for active alarms (0 indicates end of stack)
0x2E1F | AHU controller | Alarm | Standard | Alr_Released15 |  | 3x0135 | x.xx | AI94 | x.xx | 0 | 100 |  | Stack for active alarm's (0 indicate end of stack) | Stack for aktive alarmer (0 indikerer slutningen af stack) | Stack for active alarms (0 indicates end of stack)
| Humidity | Current value | Standard | Humid_ActRHOut |  | 3x0138 | 6.10 | AI263 | 6.10 | 0 | 100 |  |  |  | Actual % rel. Huminity Outdoor
| Humidity | Current value | Standard | Humid_ActRHExh |  | 3x0139 | 6.10 | AI264 | 6.10 | 0 | 100 |  |  |  | Actual % rel. Huminity Exthaust
0x2000 | AHU controller | SW version | Standard | MasterSW_Ver |  | 3x0140 | x.xx | AI95 | x.xx | 0 | 30000 |  | Master Software Ver [1/100] | Master Software Ver [1/100] | Master software version [1/100]
0x2001 | HMI display | SW version | Standard | DisplaySW_Ver |  | 3x0141 | x.xx | AI96 | x.xx | 0 | 30000 |  | Display Software Ver [1/100] | Display Software Ver [1/100] | Display software version [1/100]
0x1ED0 | Damper, Fire | Alarm | Standard | AlrFireDmpNCls |  | 3x0142 | x.xx | NA | NA | 0 | 1 |  | Alarm, Fire damper not closed | Alarm, Brandspjæld ikke lukket i forbindelse med test | Alarm, Fire damper not closed
0x1ED1 | Damper, Fire | Alarm | Standard | AlrFireDmpNOpn |  | 3x0143 | x.xx | NA | NA | 0 | 1 |  | Alarm, Fire damper not open | Alarm, Brandspjæld ikke åbnet i forbindelse med test | Alarm, Fire damper not open
0x1ED2 | Damper, Fire | Status | Standard | FireDmpTstActv |  | 3x0144 | x.xx | NA | NA | 0 | 1 |  | Fire damper test is active | Test af brandspjæld er i gang | Fire damper test is ongoing
0x2360 | Cooling, DX | Status | Standard | DX_OnTimerRE1 | Sec | 3x0145 | x.xx | AI274 | 6.41 | 0 | 600 |  | Timer for DX-Cool RE-1 ON-Periode [sec] (ExtMod-Reserve) | Timer for DX-Cool RE-1 ON-Periode [sec] (ExtMod-Reserve) | Timer for DX-Cool RE-1 ON-Periode [sec] (ExtMod-Reserve)
0x2361 | Cooling, DX | Status | Standard | DX_OnTimerRE2 | Sec | 3x0146 | x.xx | AI275 | 6.41 | 0 | 600 |  | Timer for DX-Cool RE-2 ON-Periode [sec] (ExtMod-Reserve) | Timer for DX-Cool RE-2 ON-Periode [sec] (ExtMod-Reserve) | Timer for DX-Cool RE-2 ON-Periode [sec] (ExtMod-Reserve)
0x2362 | Cooling, DX | Status | Standard | DX_OnTimerRE3 | Sec | 3x0147 | x.xx | AI276 | 6.41 | 0 | 600 |  | Timer for DX-Cool RE-3 ON-Periode [sec] (ExtMod-Reserve) | Timer for DX-Cool RE-3 ON-Periode [sec] (ExtMod-Reserve) | Timer for DX-Cool RE-3 ON-Periode [sec] (ExtMod-Reserve)
0x2363 | Cooling, DX | Status | Standard | DX_OnTimerRE4 | Sec | 3x0148 | x.xx | AI277 | 6.41 | 0 | 600 |  | Timer for DX-Cool RE-4 ON-Periode [sec] (ExtMod-Reserve) | Timer for DX-Cool RE-4 ON-Periode [sec] (ExtMod-Reserve) | Timer for DX-Cool RE-4 ON-Periode [sec] (ExtMod-Reserve)
0x2364 | Cooling, DX | Status | Standard | DX_RestartCnt1 |  | 3x0149 | x.xx | AI278 | 6.41 | 0 | 60 |  | Counter for DX-Cool RE-1 starts per hour (ExtMod-Reserve) | Tæller for DX-Cool RE-1; antal start pr. time (ExtMod-Reserve) | Counter for DX-Cool RE-1 starts per hour (ExtMod-Reserve)
0x23A0 | Heating coil 2, Water | Current value | Standard | HW2BattTemp | °C | 3x0150 | x.xx | AI279 | 6.41 | -4000 | 10000 |  | Current HeatWaterCoilTemp [1/100°C] | Varme 2: Vandflade returtemperatur [1/100°C] | Heating 2 - Hydronic coil return temperature [1/100°C]
0x2366 | Cooling, DX | Status | Standard | DX_RestartCnt3 |  | 3x0151 | x.xx | AI280 | 6.41 | 0 | 60 |  | Counter for DX-Cool RE-3 starts per hour (ExtMod-Reserve) | Tæller for DX-Cool RE-3; antal start pr. time (ExtMod-Reserve) | Counter for DX-Cool RE-3 starts per hour (ExtMod-Reserve)
0x2367 | Cooling, DX | Status | Standard | DX_RestartCnt4 |  | 3x0152 | x.xx | AI281 | 6.41 | 0 | 60 |  | Counter for DX-Cool RE-4 starts per hour (ExtMod-Reserve) | Tæller for DX-Cool RE-4; antal start pr. time (ExtMod-Reserve) | Counter for DX-Cool RE-4 starts per hour (ExtMod-Reserve)
0x2368 | Cooling, DX | Status | Standard | DX_RestartTim1 | Sec | 3x0153 | x.xx | AI282 | 6.41 | 0 | 3600 |  | Timer for DX-Cool Restart-Periode. When Timer get same as 3600/MaxRestarts per hour RestartCounter is countdown by 1 (ExtMod-Reserve) | Timer 1 for min. genstartperiode [Sec] | Timer 1 for min. restart period [sec]
0x2369 | Cooling, DX | Status | Standard | DX_RestartTim2 | Sec | 3x0154 | x.xx | AI283 | 6.41 | 0 | 3600 |  | Timer for DX-Cool Restart-Periode. When Timer get same as 3600/MaxRestarts per hour RestartCounter is countdown by 1 (ExtMod-Reserve) | Timer 2 for min. genstartperiode [Sec] | Timer 2 for min. restart period [sec]
0x236A | Cooling, DX | Status | Standard | DX_RestartTim3 | Sec | 3x0155 | x.xx | AI284 | 6.41 | 0 | 3600 |  | Timer for DX-Cool Restart-Periode. When Timer get same as 3600/MaxRestarts per hour RestartCounter is countdown by 1 (ExtMod-Reserve) | Timer 3 for min. genstartperiode [Sec] | Timer 3 for min. restart period [sec]
0x236B | Cooling, DX | Status | Standard | DX_RestartTim4 | Sec | 3x0156 | x.xx | AI285 | 6.41 | 0 | 3600 |  | Timer for DX-Cool Restart-Periode. When Timer get same as 3600/MaxRestarts per hour RestartCounter is countdown by 1 (ExtMod-Reserve) | Timer 4 for min. genstartperiode [Sec] | Timer 4 for min. restart period [sec]
0x2390 | Filter | Current value | Standard | FiltSupPrcStat | % | 3x0157 | x.xx | AI286 | 6.41 | 0 | 10000 |  | Filter actual alarmstatus for sup-filter [1/100%] DYNAMICMODE ONLY (zero in staticmode) (ExtMod-Reserve) | Aktuel alarmstatus setpunkt for filter tilluft [1/100%] | Filter actual alarmstatus for sup-filter [1/100%]
0x2391 | Filter | Current value | Standard | FiltExtPrcStat | % | 3x0158 | x.xx | AI287 | 6.41 | 0 | 10000 |  | Filter actual alarmstatus for ext-filter [1/100%] DYNAMICMODE ONLY (zero in staticmode) (ExtMod-Reserve) | Aktuel alarmstatus setpunkt for filter fraluft [1/100%] | Filter actual alarmstatus for ext-filter [1/100%]
0x2392 | Filter | Current value | Standard | FiltSupNewPa | Pa | 3x0159 | x.xx | AI288 | 6.41 | 0 | 100 |  | Filter pressure for new-filter at actual flow [Pa] DYNAMICMODE ONLY (zero in staticmode) (ExtMod-Reserve) | Filter tryk for et nyt filter ved aktuelt flow, tilluft [Pa] | Filter pressure for new-filter at actual flow [Pa]
0x2393 | Filter | Current value | Standard | FiltExtNewPa | Pa | 3x0160 | x.xx | AI289 | 6.41 | 0 | 100 |  | Filter pressure for new-filter at actual flow [Pa] DYNAMICMODE ONLY (zero in staticmode) (ExtMod-Reserve) | Filter tryk for et nyt filter ved aktuelt flow, fraluft [Pa] | Filter pressure for new-filter at actual flow [Pa]
0x2110 | Temp. sensor | Current value | Special | AddOnTSensor1 | °C | 3x0161 | x.xx | AI97 | x.xx | -4000 | 10000 |  | Additional TempSensor1 [1/100°C] | Tillægsføler 1 [1/100°C] | Add on sensor 1 [1/100°C]
0x2111 | Temp. sensor | Current value | Special | AddOnTSensor2 | °C | 3x0162 | x.xx | AI98 | x.xx | -4000 | 10000 |  | Additional TempSensor2 [1/100°C] | Tillægsføler 2 [1/100°C] | Add on sensor 2 [1/100°C]
0x2112 | Temp. sensor | Current value | Special | AddOnTSensor3 | °C | 3x0163 | x.xx | AI99 | x.xx | -4000 | 10000 |  | Additional TempSensor3 [1/100°C] | Tillægsføler 3 [1/100°C] | Add on sensor 3 [1/100°C]
0x2113 | Temp. sensor | Current value | Special | AddOnTSensor4 | °C | 3x0164 | x.xx | AI100 | x.xx | -4000 | 10000 |  | Additional TempSensor4 [1/100°C] | Tillægsføler 4 [1/100°C] | Add on sensor 4 [1/100°C]
0x2441 | Fan | Current value | Standard | MtrFanSupVin | % | NA | x.xx | AI101 | x.xx | 0 | 10000 |  | FAN-Optimize Signal [%] | 0-10VDC signal til tilluft motor | 0-10 V DC signal to supply motor
0x2442 | Fan | Current value | Standard | MtrFanExtVin | % | NA | x.xx | AI102 | x.xx | 0 | 10000 |  | 0-10VDC External Supply Motor Signal (FAN-Opt) | 0-10VDC signal til fraluft motor | 0-10 V DC signal to extract motor
0x240F | Cooling, DX | Set point | Special | ROHCondPower | % | 3x0165 | x.xx | AI290 | 6.41 | 0 | 10000 |  | Condenser Valve Power | Step-Up ventil; Effekt [1/100 %] | Only special customer code: Step-up valve - Output [1/100%]
0x23AF | Cooling, DX | Set point | Special | ROHCondOutVDC | V | 3x0166 | x.xx | AI291 | 6.41 | 0 | 10000 |  | Voltage level to step-up valve | Step-Up ventil; Spænding [1/1000 V] | Only special customer code: Step-up valve - Voltage [1/1000 V]
0x240E | Cooling, DX | Set point | Special | ROHShuntPower | % | 3x0167 | x.xx | AI292 | 6.41 | 0 | 10000 |  | Shunt Valve Power | Kondensator flade - Effekt [1/100 %] | Only special customer code: Condenser coil - Output [1/100%]
0x23AE | Cooling, DX | Set point | Special | ROHShuntOutVDC | V | 3x0168 | x.xx | AI293 | 6.41 | 0 | 10000 |  | Voltage level, to shunt valve | Shunt ventil; Spænding [1/1000 V] | Only special customer code: Shunt valve - Voltage [1/1000 V]
0x2479 | Humidifier | Set point | Standard | Humid_OutVDC | V | 3x0169 | x.xx | AI294 | 6.41 | 0 | 10000 |  | Output to SteamHuminifier [1/1000 V] | Aktuel udgang til befugter [1/1000 V] | Output to Steam Humidifier [1/1000 V]
0x247A | Humidity | Current value | Standard | Humid_ActRHSup | % | 3x0170 | x.xx | AI128 | x.xx | 0 | 10000 |  | Actual % rel. Huminity Supply | Aktuel relativ fugt i tilluft [1/100%rh] | Actual % rel. Humidity Supply duct [1/100%rh]
0x247B | Humidity | Current value | Standard | Humid_ActRHExt | % | 3x0171 | x.xx | AI127 | x.xx | 0 | 10000 |  | Actual % rel. Huminity Extract | Aktuel relativ fugt i fraluft [1/100%rh] | Actual % rel. Humidity Extract duct [1/100%rh]
0x2418 | Heating coil 12 | Set point | Special | HW12_VDCOut | mV | NA | x.xx | AI109 | x.xx | 0 | 10000 |  | Voltage level, HWB1 Out2 | Spec. kundevariant: Varmeflade udgang (1,2) VDC out | Only special customer code: Heat coil 1, step2 output (1,2) VDC out
0x24F1 | Damper, Recirculation | Status | Special | RecAltFlowAct |  | 3x0172 | x.xx | AI111 | x.xx | 0 | 2 |  | Status Chg airflow recirce | Aktuel status ændret flow omluft - 0=Ingen skift; 1=Lav til høj; 2=Høj til lav | Only special customer code: Actual status change flow recirc. - 0=No change; 1=Low to high; 2=High to low
0x24F2 | Damper, Recirculation | Status | Special | RecClosTimer | Sec | 3x0173 | x.xx | AI112 | x.xx | 0 | 7200 |  |  | Aktuel status timer for lukket recirkulering [Sec] | Only special customer code: Actual status timer for lukket recirkulering [Sec]
0x24F0 | Heating coil 2 | Status | Special | Ht2DelayTimer | Sec | 3x0174 | x.xx | AI295 | 6.41 | 0 | 7200 |  | Timer delayed heat2 | Timer forsinket Varme2 [Sec] | Only special customer code: Timer delayed Heat2 [Sec]
0x2A85 | Heat exchanger | Current value | Special | REXCPressAvg |  | 3x0175 | x.xx | AI296 | 6.41 | 0 | 2000 |  | EXC Flow Measure, Extract channel | Aktuelt trykfald målt over rotorveksler i fraluft [Pa] | Only special customer code: Actual press. drop over rotary exch. in exhaust air [Pa]
0x240A | Combi coil | Set point | Standard | CombiVDC_Out | V | 3x0176 | x.xx | AI113 | x.xx | 0 | 10000 |  | Combicoil VDC-Signal out for AfterHeat [1/1000 V] | Kombiflade VDC-Signal [1/1000 V] | Combi coil VDC-Signal [1/1000 V]
0x240B | Combi coil | Set point | Standard | CombiHeatPow | % | 3x0177 | x.xx | AI114 | x.xx | 0 | 10000 |  | CombiPower [1/100 %] | Kombiflade %-Signal varme [1/100 %] | Combi coil %-Signal heating [1/100 %]
0x240C | Combi coil | Set point | Standard | CombiCoolPow | % | NA | x.xx | AI115 | x.xx | 0 | 10000 |  | Combicoil VDC-Signal out for AfterHeat [1/1000 V] |  | Combi coil %-Signal Cooling [1/100 %]
0x240D | Combi coil | Current value | Special | HeatPmpHeatPow | % | 3x0178 | x.xx | AI297 | 6.41 | 0 | 10000 |  | HeatPump power used when heating is demanded. Otherwise CoolPower is used | Varmepumpe effekt aktiv når der er varmekrav. Ellers CoolPower [1/100 %] | Heat pump efficiency in heat demand. Else CoolPower [1/100 %]
0x2980 | Fan, Supply drive 2 | Current value | Special | EC2supMtType |  | 3x0179 | x.xx | AI298 | 6.41 | 0 | 256 |  | EC2-SupplyMotor Type | EC 2-tilluftmotor Type | Only special customer code: OJ-EC/-DV 2-supply/Supply air motor Type
0x2981 | Fan, Supply drive 2 | SW version | Special | EC2supMtEC_SW |  | 3x0180 | x.xx | AI299 | 6.41 | 0 | 1000 |  | EC2-SupplyMotor Software Ver [1/100] | EC 2-tilluftmotor Software Ver [1/100] | Only special customer code: OJ-EC/-DV 2-supply/Supply air motor Software Ver [1/100]
0x2982 | Fan, Supply drive 2 | SW version | Special | EC2supBoot_SW |  | 3x0181 | x.xx | AI300 | 6.41 | 0 | 1000 |  | EC2-SupplyMotor Boot Software Ver [1/100] | EC 2-tilluftmotor Boot Software Ver [1/100] | Only special customer code: OJ-EC/-DV 2-supply/Supply air motor Boot Software Ver [1/100]
0x2983 | Fan, Supply drive 2 | Current value | Special | EC2supMtPrcOut | % | 3x0182 | x.xx | AI301 | 6.41 | 0 | 10000 |  | EC2-SupplyMotor Percent Output [1/100%] | EC 2-tilluftmotor procent udgang [1/100%] | Only special customer code: OJ-EC/-DV 2-supply/Supply air motor percent output [1/100%]
0x2984 | Fan, Supply drive 2 | Current value | Special | EC2supMtRPMOut | RPM | 3x0183 | x.xx | AI302 | 6.41 | 0 | 10000 |  | EC2-SupplyMotor RPM Output [RPM] | EC 2-tilluftmotor aktuelt omdrejningstal [RPM] | Only special customer code: OJ-EC/-DV 2-supply/Supply air motor actual RPM [RPM]
0x2987 | Fan, Supply drive 2 | Current value | Special | EC2supMtIout | mA | 3x0184 | x.xx | AI303 | 6.41 | 0 | 30000 |  | EC2-SupplyMotor Output Current [mA] | EC 2-tilluftmotor aktuel strømudgang [mA] | Only special customer code: OJ-EC/-DV 2-supply/Supply air motor actual current output [mA]
0x2988 | Fan, Supply drive 2 | Current value | Special | EC2supMtPowOut | W | 3x0185 | x.xx | AI304 | 6.41 | 0 | 7000 |  | EC2-SupplyMotor Output Power [Watt] | EC 2-tilluftmotor aktuel effekt udgang [Watt] | Only special customer code: OJ-EC/-DV 2-supply/Supply air motor actual power output [Watt]
0x298A | Fan, Supply drive 2 | Current value | Special | EC2supDriftMin | Min | 3x0186 | x.xx | AI305 | 6.41 | 0 | 1440 |  | EC2-SupplyMotor Drifttime in minuts | EC 2-tilluftmotor antal driftminuter | Only special customer code: OJ-EC/-DV 2-supply/Supply air motor actual running time [minutes]
0x298B | Fan, Supply drive 2 | Current value | Special | EC2supDriftDay | Day | 3x0187 | x.xx | AI306 | 6.41 | 0 | 30000 |  | EC2-SupplyMotor Drifttime in days | EC 2-tilluftmotor antal driftdage | Only special customer code: OJ-EC/-DV 2-supply/Supply air motor actual running time [days]
0x298C | Fan, Supply drive 2 | Set point | Special | EC2supMtPrcSet | % | 3x0188 | x.xx | AI307 | 6.41 | 0 | 10000 |  | EC2-SupplyMotor Output Set [%] | EC 2-tilluftmotor setpunkt [1/100%] | Only special customer code: OJ-EC/-DV 2-supply/Supply air motor setpoint [1/100%]
0x2990 | Fan, Extract drive 2 | Current value | Special | EC2extMtType |  | 3x0189 | x.xx | AI308 | 6.41 | 0 | 256 |  | EC-ExtractMotor Type | EC 2-fraluftmotor Type | Only special customer code: OJ-EC/-DV 2-Extract/Exhaust air motor Type
0x2991 | Fan, Extract drive 2 | SW version | Special | EC2extMtEC_SW |  | 3x0190 | x.xx | AI309 | 6.41 | 0 | 1000 |  | EC-ExtractMotor Software Ver [1/100] | EC 2-fraluftmotor Software Ver [1/100] | Only special customer code: OJ-EC/-DV 2-Extract/Exhaust air motor Software Ver [1/100]
0x2992 | Fan, Extract drive 2 | SW version | Special | EC2extBoot_SW |  | 3x0191 | x.xx | AI310 | 6.41 | 0 | 1000 |  | EC-ExtractMotor Boot Software Ver [1/100] | EC 2-fraluftmotor Boot Software Ver [1/100] | Only special customer code: OJ-EC/-DV 2-Extract/Exhaust air motor Boot Software Ver [1/100]
0x2993 | Fan, Extract drive 2 | Current value | Special | EC2extMtPrcOut | % | 3x0192 | x.xx | AI311 | 6.41 | 0 | 10000 |  | EC-ExtractMotor Percent Output [1/100%] | EC 2-fraluftmotor procent udgang [1/100%] | Only special customer code: OJ-EC/-DV 2-Extract/Exhaust air motor percent output [1/100%]
0x2994 | Fan, Extract drive 2 | Current value | Special | EC2extMtRPMOut | RPM | 3x0193 | x.xx | AI312 | 6.41 | 0 | 10000 |  | EC-ExtractMotor RPM Output [RPM] | EC 2-fraluftmotor aktuelt omdrejningstal [RPM] | Only special customer code: OJ-EC/-DV 2-Extract/Exhaust air motor actual RPM [RPM]
0x2997 | Fan, Extract drive 2 | Current value | Special | EC2extMtIout | mA | 3x0194 | x.xx | AI313 | 6.41 | 0 | 30000 |  | EC-ExtractMotor Output Current [mA] | EC 2-fraluftmotor aktuel strømudgang [mA] | Only special customer code: OJ-EC/-DV 2-Extract/Exhaust air motor actual current output [mA]
0x2998 | Fan, Extract drive 2 | Current value | Special | EC2extMtPowOut | W | 3x0195 | x.xx | AI314 | 6.41 | 0 | 7000 |  | EC-ExtractMotor Output Power [Watt] | EC 2-fraluftmotor aktuel effekt udgang [Watt] | Only special customer code: OJ-EC/-DV 2-Extract/Exhaust air motor actual power output [Watt]
0x299A | Fan, Extract drive 2 | Current value | Special | EC2extDriftMin | Min | 3x0196 | x.xx | AI315 | 6.41 | 0 | 1440 |  | EC-ExtractMotor Drifttime in minuts | EC 2-fraluftmotor antal driftminuter | Only special customer code: OJ-EC/-DV 2-Extract/Exhaust air motor actual running time [minutes]
0x299B | Fan, Extract drive 2 | Current value | Special | EC2extDriftDay | Day | 3x0197 | x.xx | AI316 | 6.41 | 0 | 30000 |  | EC-ExtractMotor Drifttime in days | EC 2-fraluftmotor antal driftdage | Only special customer code: OJ-EC/-DV 2-Extract/Exhaust air motor actual running time [days]
0x299C | Fan, Extract drive 2 | Set point | Special | EC2extMtPrcSet | % | 3x0198 | x.xx | AI317 | 6.41 | 0 | 10000 |  | EC-ExtractMotor Output Set [%] | EC 2-fraluftmotor setpunkt [1/100%] | Only special customer code: OJ-EC/-DV 2-Extract/Exhaust air motor setpoint [1/100%]
0x2960 | Fan, Supply drive | Current value | Standard | ECsupMtrType |  | 3x0200 | x.xx | AI318 | 6.41 | 0 | 256 |  | EC-SupplyMotor Type | EC-tilluftmotor Type | OJ-EC/-DV-supply/Supply air motor Type
0x2961 | Fan, Supply drive | SW version | Standard | ECsupMtrFC_SW |  | 3x0201 | x.xx | AI319 | 6.41 | 0 | 1000 |  | EC-SupplyMotor Software Ver [1/100] | EC-tilluftmotor Software Ver [1/100] | OJ-EC/-DV-supply/Supply air motor Software Ver [1/100]
0x2962 | Fan, Supply drive | SW version | Standard | ECsupBoot_SW |  | 3x0202 | x.xx | AI320 | 6.41 | 0 | 1000 |  | EC-SupplyMotor Boot Software Ver [1/100] | EC-tilluftmotor Boot Software Ver [1/100] | OJ-EC/-DV-supply/Supply air motor Boot Software Ver [1/100]
0x2963 | Fan, Supply drive | Current value | Standard | ECsupMtrPrcOut | % | 3x0203 | x.xx | AI321 | 6.41 | 0 | 10000 |  | EC-SupplyMotor Percent Output [1/100%] | EC-tilluftmotor procent udgang [1/100%] | OJ-EC/-DV-supply/Supply air motor procent udgang [1/100%]
0x2964 | Fan, Supply drive | Current value | Standard | ECsupMtrRPMOut | RPM | 3x0204 | x.xx | AI322 | 6.41 | 0 | 10000 |  | EC-SupplyMotor RPM Output [RPM] | EC-tilluftmotor aktuelt omdrejningstal [RPM] | OJ-EC/-DV-supply/Supply air motor actual RPM [RPM]
0x2967 | Fan, Supply drive | Current value | Standard | ECsupMtrIout | mA | 3x0205 | x.xx | AI323 | 6.41 | 0 | 30000 |  | EC-SupplyMotor Output Current [mA] | EC-tilluftmotor aktuel strømudgang [mA] | OJ-EC/-DV-supply/Supply air motor actual current output [1/100mA]
0x2968 | Fan, Supply drive | Current value | Standard | ECsupMtrPowOut | W | 3x0206 | x.xx | NA | NA | 0 | 7000 |  | EC-SupplyMotor Output Power [Watt] | EC-tilluftmotor aktuel effekt udgang [Watt] | OJ-EC/-DV-supply/Supply air motor actual power output [Watt]
0x296A | Fan, Supply drive | Current value | Standard | ECsupDriftMin | Min | 3x0207 | x.xx | AI324 | 6.41 | 0 | 1440 |  | EC-SupplyMotor Drifttime in minuts | EC-tilluftmotor antal driftminuter | OJ-EC/-DV-supply/Supply air motor actual running time [minutes]
0x296B | Fan, Supply drive | Current value | Standard | ECsupDriftDay | Day | 3x0208 | x.xx | AI325 | 6.41 | 0 | 30000 |  | EC-SupplyMotor Drifttime in days | EC-tilluftmotor antal driftdage | OJ-EC/-DV-supply/Supply air motor actual running time [days]
0x296C | Fan, Supply drive | Set point | Standard | ECsupMtrPrcSet | % | 3x0209 | x.xx | AI326 | 6.41 | 0 | 10000 |  | EC-SupplyMotor Output Set [%] | EC-tilluftmotor setpunkt [1/100%] | OJ-EC/-DV-supply/Supply air motor setpoint [1/100%]
0x2972 | Fan, Extract drive | SW version | Standard | ECextBoot_SW |  | 3x0210 | x.xx | AI327 | 6.41 | 0 | 1000 |  | EC-ExtractMotor Boot Software Ver [1/100] | EC-fraluftmotor Boot Software Ver [1/100] | OJ-EC/-DV-Extract/Exhaust air motor Boot Software Ver [1/100]
0x2973 | Fan, Extract drive | Current value | Standard | ECextMtrPrcOut | % | 3x0211 | x.xx | AI328 | 6.41 | 0 | 10000 |  | EC-ExtractMotor Percent Output [1/100%] | EC-fraluftmotor procent udgang [1/100%] | OJ-EC/-DV-Extract/Exhaust air motor procent udgang [1/100%]
0x2974 | Fan, Extract drive | Current value | Standard | ECextMtrRPMOut | RPM | 3x0212 | x.xx | AI329 | 6.41 | 0 | 10000 |  | EC-ExtractMotor RPM Output [RPM] | EC-fraluftmotor aktuelt omdrejningstal [RPM] | OJ-EC/-DV-Extract/Exhaust air motor actual RPM [RPM]
0x2977 | Fan, Extract drive | Current value | Standard | ECextMtrIout | mA | 3x0213 | x.xx | AI330 | 6.41 | 0 | 30000 |  | EC-ExtractMotor Output Current [mA] | EC-fraluftmotor aktuel strømudgang [mA] | OJ-EC/-DV-Extract/Exhaust air motor actual current output [1/100mA]
0x2978 | Fan, Extract drive | Current value | Standard | ECextMtrPowOut | W | 3x0214 | x.xx | NA | NA | 0 | 7000 |  | EC-ExtractMotor Output Power [Watt] | EC-fraluftmotor aktuel effekt udgang [Watt] | OJ-EC/-DV-Extract/Exhaust air motor actual power output [Watt]
0x297A | Fan, Extract drive | Current value | Standard | ECextDriftMin | Min | 3x0215 | x.xx | AI331 | 6.41 | 0 | 1440 |  | EC-ExtractMotor Drifttime in minuts | EC-fraluftmotor antal driftminuter | OJ-EC/-DV-Extract/Exhaust air motor actual running time [minutes]
0x297B | Fan, Extract drive | Current value | Standard | ECextDriftDay | Day | 3x0216 | x.xx | AI332 | 6.41 | 0 | 30000 |  | EC-ExtractMotor Drifttime in days | EC-fraluftmotor antal driftdage | OJ-EC/-DV-Extract/Exhaust air motor actual running time [days]
0x297C | Fan, Extract drive | Current value | Standard | ECextMtrPrcSet | % | 3x0217 | x.xx | AI333 | 6.41 | 0 | 10000 |  | EC-ExtractMotor Output Set [%] | EC-fraluftmotor setpunkt [1/100%] | OJ-EC/-DV-Extract/Exhaust air motor setpoint [1/100%]
0x2970 | Fan, Extract drive | Current value | Standard | ECextMtrType |  | 3x0218 | x.xx | AI334 | 6.41 | 0 | 256 |  | EC-ExtractMotor Type | EC-fraluftmotor Type | OJ-EC/-DV-Extract/Exhaust air motor Type
0x2971 | Fan, Extract drive | SW version | Standard | ECextMtrFC_SW |  | 3x0219 | x.xx | AI335 | 6.41 | 0 | 1000 |  | EC-ExtractMotor Software Ver [1/100] | EC-fraluftmotor Software Ver [1/100] | OJ-EC/-DV-Extract/Exhaust air motor Software Ver [1/100]
0x2104 | Temp. Supply 2 | Current value | Standard | SupplyTemp2 | °C | 3x0220 | x.xx | AI234 | 5.07 | -4000 | 10000 |  | Current SupplyTemp2 [1/100°C] | Aktuel tilluftstemperatur2 [1/100°C] - Spec. kundevariant | Only special customer code: Actual supply supply temperature2 [1/100°C]
0x2304 | Temp. out door | Current value | Standard | ExtOutDTemp | °C | 3x0221 | x.xx | AI118 | x.xx | -6000 | 10000 |  | Current external OutDoorTemp [1/100°C] | Ekstern udetemperaturføler [1/100°C] | External outdoor temperature sensor [1/100°C]
0x2410 | Preheater coil | Current value | Standard | PHeatTempAir | °C | 3x0222 | x.xx | AI119 | x.xx | -4000 | 10000 |  | Current AirTemp after Preheater [1/100°C] | Temperatur efter forvarmeflade [1/100 °C] | Temperature after pre-heating coil [1/100 °C]
0x2352 | Cooling coil | Current value | Standard | CW_supplyTemp | °C | 3x0223 | x.xx | AI120 | x.xx | -4000 | 10000 |  | Current CoolWaterCoilTemp [1/100°C] | Fremløb køleflade [1/100 °C] | Cold water supply temperature for cooling coil [1/100 °C]
0x23D0 | Damper, Recirculation | Status | Standard | RecFreshAirDis | % | 3x0224 | x.xx | AI121 | x.xx | 0 | 10000 |  | Display value Damper position without corrections | Spjældstilling frisk luft [1/100 %] | Damper position intake/outdoor damper [1/100 %]
0x23D1 | Damper, Recirculation | Status | Standard | RecDampPrcDis | % | 3x0225 | x.xx | AI122 | x.xx | 0 | 10000 |  | Display value Damper position without corrections | Spjældstilling recirkulation [1/100 %] | Damper position recirkulation [1/100 %]
0x242C | Cooling coil | Set point | Standard | CoolVDC_Out2 | V | 3x0226 | x.xx | AI123 | x.xx | 0 | 10000 |  | Cool VDC-Signal out 2 for CoolAgg. [1/1000 V] | Udgangsspænding køleventil [1/1000 V] | Output voltage cooling valve2 (only combi coil) [1/1000 V]
0x2AF9 | Fan, ATV drive | Current value | Special | AtvExtPower | kW | 3x0227 | x.xx | AI116 | x.xx | 0 | 30000 |  | ExtractMotor Input Power [KiloWatt] | ATV Fraluft udgangseffekt [1/100 kW] | ATV extract air actual power [1/100 kW]
0x2AF1 | Fan, ATV drive | Current value | Special | AtvSupPower | kW | 3x0228 | x.xx | AI117 | x.xx | 0 | 30000 |  | SupplyMotor Input Power [KiloWatt] | ATV Tilluft udgangseffekt [1/100 kW] | ATV supply air actual power [1/100 kW]
|  |  | Standard | OutDoorSenTemp |  | 3x0229 | 5.07 | AI233 | 5.07 | 0 | 4000 |  |  |  | Current OutDoorTemp [1/100C]
0x2107 | Filter | Status | Standard | OutFilRestDay |  | 3x0230 | x.xx | AI124 | x.xx | 0 | 366 |  | Outdoor restime before filtershift alarm activated | Resterende dage til alarm for tilluft filterskift | Days until timer alarm from the outdoor filter
0x2227 | Filter | Status | Standard | ExtFilRestDay |  | 3x0231 | x.xx | AI125 | x.xx | 0 | 366 |  | Extract restime before filtershift alarm activated | Resterende dage til alarm for fraluft filterskift | Days until timer alarm from the extract filter
0x23A7 | Combi coil | Current value | Standard | CombiBattTemp | °C | NA | x.xx | AI126 | x.xx | -4000 | 10000 |  | Current HeatWaterCoilTemp [1/100°C] | Kombiflade - Aktuel returtemperatur [1/100°C] | combi coil - Actual return temperature [1/100°C]
0x248C | Humidity | Current value | Standard | RelHumMixed | % | 3x0232 | x.xx | AI129 | x.xx | 0 | 10000 |  | Rel. Humidity Mixedair | Aktuel relativ fugt i mixed luft [1/100%rh] | Actual relative humidity in mixed air [1/100%rh]
0x210A | Filter | Status | Standard | SupFi2RestDay |  | 3x0233 | 4.18 | AI336 | 6.41 | 0 | 366 |  | Supply filter 2 restime before filtershift alarm activated | Tilluft filter 2 Restid indtil filterskift alarm aktiveres | Supply filter 2: Restime before change filter alarm will be activated
0x222A | Filter | Status | Standard | ExtFil2RestDay |  | 3x0234 | 4.18 | AI337 | 6.41 | 0 | 366 |  | Extract filter 2 restime before filtershift alarm activated | Fraluft filter 2 Restid indtil filterskift alarm aktiveres | Extract filter 2: Restime before change filter alarm will be activated
| Zone | Status | Standard | ZM_Count |  | 3x0235 | 4.19 | AI132 | 4.19 | 0 | 4 |  |  |  | Number of Detected ZoneModules
| Zone | Status | Standard | ZM_OpMode |  | 3x0236 | 4.19 | AI133 | 4.19 | 0 | 7 |  |  |  | ZoneControl Operation Mode
| Zone 1 | Status | Standard | ZM1_Status |  | 3x0237 | 4.19 | AI134 | 4.19 | 0 | 2 |  |  |  | ZoneModule 1 - Status: 0=No active alarm; 1=A-alarm active; 2=B-alarm active
| Zone 1 | Status | Standard | ZM1_Sup1Set |  | 3x0238 | 4.19 | AI135 | 4.19 | 0 | 0 |  |  |  | ZoneModule 1 - VAV Supply 1 Actuator Setpoint [scale depending on the connected actuator]
| Zone 1 | Status | Standard | ZM1_Sup1Flow |  | 3x0239 | 4.19 | AI136 | 4.19 | 0 | 0 |  |  |  | ZoneModule 1 - VAV Supply 1 Actuator Flow [scale depending on the connected actuator]
| Zone 1 | Status | Standard | ZM1_Sup2Set |  | 3x0240 | 4.19 | AI137 | 4.19 | 0 | 0 |  |  |  | ZoneModule 1 - VAV Supply 2 Actuator Setpoint [scale depending on the connected actuator]
| Zone 1 | Status | Standard | ZM1_Sup2Flow |  | 3x0241 | 4.19 | AI138 | 4.19 | 0 | 0 |  |  |  | ZoneModule 1 - VAV Supply 2 Actuator Flow [scale depending on the connected actuator]
| Zone 1 | Status | Standard | ZM1_ExtSet |  | 3x0242 | 4.19 | AI139 | 4.19 | 0 | 0 |  |  |  | ZoneModule 1 - VAV Extract Actuator Setpoint [scale depending on the connected actuator]
| Zone 1 | Status | Standard | ZM1_ExtFlow |  | 3x0243 | 4.19 | AI140 | 4.19 | 0 | 0 |  |  |  | ZoneModule 1 - VAV Extract Actuator Flow [scale depending on the connected actuator]
| Zone 1 | Status | Standard | ZM1_HeatSet |  | 3x0244 | 4.19 | AI141 | 4.19 | 0 | 0 |  |  |  | ZoneModule 1 - VAV Heating Actuator Setpoint [scale depending on the connected actuator]
| Zone 1 | Status | Standard | ZM1_HeatFlow |  | 3x0245 | 4.19 | AI142 | 4.19 | 0 | 0 |  |  |  | ZoneModule 1 - VAV Heating Actuator Flow [scale depending on the connected actuator]
| Zone 1 | Status | Standard | ZM1_CoolSet |  | 3x0246 | 4.19 | AI143 | 4.19 | 0 | 0 |  |  |  | ZoneModule 1 - VAV Cooling Actuator Setpoint [scale depending on the connected actuator]
| Zone 1 | Status | Standard | ZM1_CoolFlow |  | 3x0247 | 4.19 | AI144 | 4.19 | 0 | 0 |  |  |  | ZoneModule 1 - VAV Heating Actuator Flow [scale depending on the connected actuator]
| Zone 1 | Status | Standard | ZM1_RoomTemp |  | 3x0248 | 4.19 | AI145 | 4.19 | -4000 | 10000 |  |  |  | ZoneModule 1 - Room Temperature Value [1/100°C]
| Zone 1 | Status | Standard | ZM1_SupTemp |  | 3x0249 | 4.19 | AI146 | 4.19 | -4000 | 10000 |  |  |  | ZoneModule 1 - Supply Temperature Value [1/100°C]
| Zone 1 | Status | Standard | ZM1_SetOffset |  | 3x0250 | 4.19 | AI147 | 4.19 | -4000 | 10000 |  |  |  | ZoneModule 1 - Remote Setpoint Offset [1/100°C]
| Zone 1 | Status | Standard | ZM1_CO2VOC |  | 3x0251 | 4.19 | AI148 | 4.19 | 0 | 5000 |  |  |  | ZoneModule 1 - CO2/VOC Value [ppm]
| Zone 1 | Status | Standard | ZM1_RH |  | 3x0252 | 4.19 | AI149 | 4.19 | 0 | 10000 |  |  |  | ZoneModule 1 - RH Value [1/100%rh]
| Zone 2 | Status | Standard | ZM2_Status |  | 3x0253 | 4.19 | AI150 | 4.19 | 0 | 2 |  |  |  | ZoneModule 2 - Status: 0=No active alarm; 1=A-alarm active; 2=B-alarm active
| Zone 2 | Status | Standard | ZM2_Sup1Set |  | 3x0254 | 4.19 | AI151 | 4.19 | 0 | 0 |  |  |  | ZoneModule 2 - VAV Supply 1 Actuator Setpoint [scale depending on the connected actuator]
| Zone 2 | Status | Standard | ZM2_Sup1Flow |  | 3x0255 | 4.19 | AI152 | 4.19 | 0 | 0 |  |  |  | ZoneModule 2 - VAV Supply 1 Actuator Flow [scale depending on the connected actuator]
| Zone 2 | Status | Standard | ZM2_Sup2Set |  | 3x0256 | 4.19 | AI153 | 4.19 | 0 | 0 |  |  |  | ZoneModule 2 - VAV Supply 2 Actuator Setpoint [scale depending on the connected actuator]
| Zone 2 | Status | Standard | ZM2_Sup2Flow |  | 3x0257 | 4.19 | AI154 | 4.19 | 0 | 0 |  |  |  | ZoneModule 2 - VAV Supply 2 Actuator Flow [scale depending on the connected actuator]
| Zone 2 | Status | Standard | ZM2_ExtSet |  | 3x0258 | 4.19 | AI155 | 4.19 | 0 | 0 |  |  |  | ZoneModule 2 - VAV Extract Actuator Setpoint [scale depending on the connected actuator]
| Zone 2 | Status | Standard | ZM2_ExtFlow |  | 3x0259 | 4.19 | AI156 | 4.19 | 0 | 0 |  |  |  | ZoneModule 2 - VAV Extract Actuator Flow [scale depending on the connected actuator]
| Zone 2 | Status | Standard | ZM2_HeatSet |  | 3x0260 | 4.19 | AI157 | 4.19 | 0 | 0 |  |  |  | ZoneModule 2 - VAV Heating Actuator Setpoint [scale depending on the connected actuator]
| Zone 2 | Status | Standard | ZM2_HeatFlow |  | 3x0261 | 4.19 | AI158 | 4.19 | 0 | 0 |  |  |  | ZoneModule 2 - VAV Heating Actuator Flow [scale depending on the connected actuator]
| Zone 2 | Status | Standard | ZM2_CoolSet |  | 3x0262 | 4.19 | AI159 | 4.19 | 0 | 0 |  |  |  | ZoneModule 2 - VAV Cooling Actuator Setpoint [scale depending on the connected actuator]
| Zone 2 | Status | Standard | ZM2_CoolFlow |  | 3x0263 | 4.19 | AI160 | 4.19 | 0 | 0 |  |  |  | ZoneModule 2 - VAV Cooling Actuator Flow [scale depending on the connected actuator]
| Zone 2 | Status | Standard | ZM2_RoomTemp |  | 3x0264 | 4.19 | AI161 | 4.19 | -4000 | 10000 |  |  |  | ZoneModule 2 - Room Temperature Value [1/100°C]
| Zone 2 | Status | Standard | ZM2_SupTemp |  | 3x0265 | 4.19 | AI162 | 4.19 | -4000 | 10000 |  |  |  | ZoneModule 2 - Supply Temperature Value [1/100°C]
| Zone 2 | Status | Standard | ZM2_SetOffset |  | 3x0266 | 4.19 | AI163 | 4.19 | -4000 | 10000 |  |  |  | ZoneModule 2 - Remote Setpoint Offset [1/100°C]
| Zone 2 | Status | Standard | ZM2_CO2VOC |  | 3x0267 | 4.19 | AI164 | 4.19 | 0 | 5000 |  |  |  | ZoneModule 2 - CO2/VOC Value [ppm]
| Zone 2 | Status | Standard | ZM2_RH |  | 3x0268 | 4.19 | AI165 | 4.19 | 0 | 10000 |  |  |  | ZoneModule 2 - RH Value [1/100%rh]
| Zone 3 | Status | Standard | ZM3_Status |  | 3x0269 | 4.19 | AI166 | 4.19 | 0 | 2 |  |  |  | ZoneModule 3 - Status: 0=No active alarm; 1=A-alarm active; 2=B-alarm active
| Zone 3 | Status | Standard | ZM3_Sup1Set |  | 3x0270 | 4.19 | AI167 | 4.19 | 0 | 0 |  |  |  | ZoneModule 3 - VAV Supply 1 Actuator Setpoint [scale depending on the connected actuator]
| Zone 3 | Status | Standard | ZM3_Sup1Flow |  | 3x0271 | 4.19 | AI168 | 4.19 | 0 | 0 |  |  |  | ZoneModule 3 - VAV Supply 1 Actuator Flow [scale depending on the connected actuator]
| Zone 3 | Status | Standard | ZM3_Sup2Set |  | 3x0272 | 4.19 | AI169 | 4.19 | 0 | 0 |  |  |  | ZoneModule 3 - VAV Supply 2 Actuator Setpoint [scale depending on the connected actuator]
| Zone 3 | Status | Standard | ZM3_Sup2Flow |  | 3x0273 | 4.19 | AI170 | 4.19 | 0 | 0 |  |  |  | ZoneModule 3 - VAV Supply 2 Actuator Flow [scale depending on the connected actuator]
| Zone 3 | Status | Standard | ZM3_ExtSet |  | 3x0274 | 4.19 | AI171 | 4.19 | 0 | 0 |  |  |  | ZoneModule 3 - VAV Extract Actuator Setpoint [scale depending on the connected actuator]
| Zone 3 | Status | Standard | ZM3_ExtFlow |  | 3x0275 | 4.19 | AI172 | 4.19 | 0 | 0 |  |  |  | ZoneModule 3 - VAV Extract Actuator Flow [scale depending on the connected actuator]
| Zone 3 | Status | Standard | ZM3_HeatSet |  | 3x0276 | 4.19 | AI173 | 4.19 | 0 | 0 |  |  |  | ZoneModule 3 - VAV Heating Actuator Setpoint [scale depending on the connected actuator]
| Zone 3 | Status | Standard | ZM3_HeatFlow |  | 3x0277 | 4.19 | AI174 | 4.19 | 0 | 0 |  |  |  | ZoneModule 3 - VAV Heating Actuator Flow [scale depending on the connected actuator]
| Zone 3 | Status | Standard | ZM3_CoolSet |  | 3x0278 | 4.19 | AI175 | 4.19 | 0 | 0 |  |  |  | ZoneModule 3 - VAV Cooling Actuator Setpoint [scale depending on the connected actuator]
| Zone 3 | Status | Standard | ZM3_CoolFlow |  | 3x0279 | 4.19 | AI176 | 4.19 | 0 | 0 |  |  |  | ZoneModule 3 - VAV Cooling Actuator Flow [scale depending on the connected actuator]
| Zone 3 | Status | Standard | ZM3_RoomTemp |  | 3x0280 | 4.19 | AI177 | 4.19 | -4000 | 10000 |  |  |  | ZoneModule 3 - Room Temperature Value [1/100°C]
| Zone 3 | Status | Standard | ZM3_SupTemp |  | 3x0281 | 4.19 | AI178 | 4.19 | -4000 | 10000 |  |  |  | ZoneModule 3 - Supply Temperature Value [1/100°C]
| Zone 3 | Status | Standard | ZM3_SetOffset |  | 3x0282 | 4.19 | AI179 | 4.19 | -4000 | 10000 |  |  |  | ZoneModule 3 - Remote Setpoint Offset [1/100°C]
| Zone 3 | Status | Standard | ZM3_CO2VOC |  | 3x0283 | 4.19 | AI180 | 4.19 | 0 | 5000 |  |  |  | ZoneModule 3 - CO2/VOC Value [ppm]
| Zone 3 | Status | Standard | ZM3_RH |  | 3x0284 | 4.19 | AI181 | 4.19 | 0 | 10000 |  |  |  | ZoneModule 3 - RH Value [1/100%rh]
| Zone 4 | Status | Standard | ZM4_Status |  | 3x0285 | 4.19 | AI182 | 4.19 | 0 | 2 |  |  |  | ZoneModule 4 - Status: 0=No active alarm; 1=A-alarm active; 2=B-alarm active
| Zone 4 | Status | Standard | ZM4_Sup1Set |  | 3x0286 | 4.19 | AI183 | 4.19 | 0 | 0 |  |  |  | ZoneModule 4 - VAV Supply 1 Actuator Setpoint [scale depending on the connected actuator]
| Zone 4 | Status | Standard | ZM4_Sup1Flow |  | 3x0287 | 4.19 | AI184 | 4.19 | 0 | 0 |  |  |  | ZoneModule 4 - VAV Supply 1 Actuator Flow [scale depending on the connected actuator]
| Zone 4 | Status | Standard | ZM4_Sup2Set |  | 3x0288 | 4.19 | AI185 | 4.19 | 0 | 0 |  |  |  | ZoneModule 4 - VAV Supply 2 Actuator Setpoint [scale depending on the connected actuator]
| Zone 4 | Status | Standard | ZM4_Sup2Flow |  | 3x0289 | 4.19 | AI186 | 4.19 | 0 | 0 |  |  |  | ZoneModule 4 - VAV Supply 2 Actuator Flow [scale depending on the connected actuator]
| Zone 4 | Status | Standard | ZM4_ExtSet |  | 3x0290 | 4.19 | AI187 | 4.19 | 0 | 0 |  |  |  | ZoneModule 4 - VAV Extract Actuator Setpoint [scale depending on the connected actuator]
| Zone 4 | Status | Standard | ZM4_ExtFlow |  | 3x0291 | 4.19 | AI188 | 4.19 | 0 | 0 |  |  |  | ZoneModule 4 - VAV Extract Actuator Flow [scale depending on the connected actuator]
| Zone 4 | Status | Standard | ZM4_HeatSet |  | 3x0292 | 4.19 | AI189 | 4.19 | 0 | 0 |  |  |  | ZoneModule 4 - VAV Heating Actuator Setpoint [scale depending on the connected actuator]
| Zone 4 | Status | Standard | ZM4_HeatFlow |  | 3x0293 | 4.19 | AI190 | 4.19 | 0 | 0 |  |  |  | ZoneModule 4 - VAV Heating Actuator Flow [scale depending on the connected actuator]
| Zone 4 | Status | Standard | ZM4_CoolSet |  | 3x0294 | 4.19 | AI191 | 4.19 | 0 | 0 |  |  |  | ZoneModule 4 - VAV Cooling Actuator Setpoint [scale depending on the connected actuator]
| Zone 4 | Status | Standard | ZM4_CoolFlow |  | 3x0295 | 4.19 | AI192 | 4.19 | 0 | 0 |  |  |  | ZoneModule 4 - VAV Cooling Actuator Flow [scale depending on the connected actuator]
| Zone 4 | Status | Standard | ZM4_RoomTemp |  | 3x0296 | 4.19 | AI193 | 4.19 | -4000 | 10000 |  |  |  | ZoneModule 4 - Room Temperature Value [1/100°C]
| Zone 4 | Status | Standard | ZM4_SupTemp |  | 3x0297 | 4.19 | AI194 | 4.19 | -4000 | 10000 |  |  |  | ZoneModule 4 - Supply Temperature Value [1/100°C]
| Zone 4 | Status | Standard | ZM4_SetOffset |  | 3x0298 | 4.19 | AI195 | 4.19 | -4000 | 10000 |  |  |  | ZoneModule 4 - Remote Setpoint Offset [1/100°C]
| Zone 4 | Status | Standard | ZM4_CO2VOC |  | 3x0299 | 4.19 | AI196 | 4.19 | 0 | 5000 |  |  |  | ZoneModule 4 - CO2/VOC Value [ppm]
| Zone 4 | Status | Standard | ZM4_RH |  | 3x0300 | 4.19 | AI197 | 4.19 | 0 | 10000 |  |  |  | ZoneModule 4 - RH Value [1/100%rh]
| CVM Meter | Status | Standard | CVMVoltageL1 |  | 3x0301 | 4.21 | AI198 | 4.21 | 0 | 5200 |  |  |  | CVM Phase L1 to neutral (N) voltage [V]
| CVM Meter | Status | Standard | CVMCurrentL1 |  | 3x0302 | 4.21 | AI199 | 4.21 | 0 | 6000 |  |  |  | CVM Current L1 value [A]
| CVM Meter | Status | Standard | CVMActPowerL1 |  | 3x0303 | 4.21 | AI200 | 4.21 | 0 | 65535 |  |  |  | CVM Active power [kW]
| CVM Meter | Status | Standard | CVMVoltageL2 |  | 3x0304 | 4.21 | AI201 | 4.21 | 0 | 5200 |  |  |  | CVM Phase L2 to neutral (N) voltage [V]
| CVM Meter | Status | Standard | CVMCurrentL2 |  | 3x0305 | 4.21 | AI202 | 4.21 | 0 | 6000 |  |  |  | CVM Current L2 value [A]
| CVM Meter | Status | Standard | CVMActPowerL2 |  | 3x0306 | 4.21 | AI203 | 4.21 | 0 | 65535 |  |  |  | CVM Active power [kW]
| CVM Meter | Status | Standard | CVMVoltageL3 |  | 3x0307 | 4.21 | AI204 | 4.21 | 0 | 5200 |  |  |  | CVM Phase L3 to neutral (N) voltage [V]
| CVM Meter | Status | Standard | CVMCurrentL3 |  | 3x0308 | 4.21 | AI205 | 4.21 | 0 | 6000 |  |  |  | CVM Current L3 value [A]
| CVM Meter | Status | Standard | CVMActPowerL3 |  | 3x0309 | 4.21 | AI206 | 4.21 | 0 | 65535 |  |  |  | CVM Active power [kW]
| CVM Meter | Status | Standard | CVMActPowerIII |  | 3x0310 | 4.21 | AI207 | 4.21 | 0 | 65535 |  |  |  | CVM Active power three phases [W] (Low Byte)
| CVM Meter | Status | Standard | CVMFrequency |  | 3x0311 | 4.21 | AI208 | 4.21 | 0 | 600 |  |  |  | CVM Frequency value [Hz]
| CVM Meter | Status | Standard | CVMVoltageL1L2 |  | 3x0312 | 4.21 | AI209 | 4.21 | 0 | 5200 |  |  |  | CVM Phase-phase Voltage L1 to L2 [V]
| CVM Meter | Status | Standard | CVMVoltageL2L3 |  | 3x0313 | 4.21 | AI210 | 4.21 | 0 | 5200 |  |  |  | CVM Phase-phase Voltage L2 to L3 [V]
| CVM Meter | Status | Standard | CVMVoltageL3L1 |  | 3x0314 | 4.21 | AI211 | 4.21 | 0 | 5200 |  |  |  | CVM Phase-phase Voltage L3 to L1 [V]
| CVM Meter | Status | Standard | CVMActEnergIII |  | 3x0315 | 4.26 | AI230 | 5.07 | 0 | 65535 |  |  |  | CVM Active energy three phases [kWh]
| CVM Meter | Status | Standard | CVMCurrentL1H |  | 3x0316 | 5.07 | AI235 | 5.07 | 0 | 65535 |  |  |  | CVM Current value [mA] - Note!: Values are calculated as (High byte) x 65536 + (Low byte) - High and low bytes = Integer
| CVM Meter | Status | Standard | CVMActPowerL1H |  | 3x0317 | 5.07 | AI236 | 5.07 | 0 | 65535 |  |  |  | CVM Active power [W] - Note!: Values are calculated as (High byte) x 65536 + (Low byte) - High and low bytes = Integer
| CVM Meter | Status | Standard | CVMCurrentL2H |  | 3x0318 | 5.07 | AI237 | 5.07 | 0 | 65535 |  |  |  | CVM Current value [mA] - Note!: Values are calculated as (High byte) x 65536 + (Low byte) - High and low bytes = Integer
| CVM Meter | Status | Standard | CVMActPowerL2H |  | 3x0319 | 5.07 | AI238 | 5.07 | 0 | 65535 |  |  |  | CVM Active power [W] - Note!: Values are calculated as (High byte) x 65536 + (Low byte) - High and low bytes = Integer
| CVM Meter | Status | Standard | CVMCurrentL3H |  | 3x0320 | 5.07 | AI239 | 5.07 | 0 | 65535 |  |  |  | CVM Current value [mA] - Note!: Values are calculated as (High byte) x 65536 + (Low byte) - High and low bytes = Integer
| CVM Meter | Status | Standard | CVMActPowerL3H |  | 3x0321 | 5.07 | AI240 | 5.07 | 0 | 65535 |  |  |  | CVM Active power [W] - Note!: Values are calculated as (High byte) x 65536 + (Low byte) - High and low bytes = Integer
| CVM Meter | Status | Standard | CVMActPoweIIIH |  | 3x0322 | 5.07 | AI241 | 5.07 | 0 | 65535 |  |  |  | CVM Active power three phases [W] (High Byte) - Note!: Values are calculated as (High byte) x 65536 + (Low byte) - High and low bytes = Integer
| CVM Meter | Status | Standard | CVMActEnerIIIH |  | 3x0323 | 5.07 | AI242 | 5.07 | 0 | 65535 |  |  |  | CVM Active energy three phases [Wh] - Note!: Values are calculated as (High byte) x 65536 + (Low byte) - High and low bytes = Integer
| CVM Meter | Status | Standard | CCVMVoltageL1 |  | 3x0330 | 4.21 | AI212 | 4.21 | 0 | 5200 |  |  |  | CCVM Cool Phase L1 to neutral (N) voltage [V]
| CVM Meter | Status | Standard | CCVMCurrentL1 |  | 3x0331 | 4.21 | AI213 | 4.21 | 0 | 6000 |  |  |  | CCVM Cool Current L1 value [A]
| CVM Meter | Status | Standard | CCVMActPowerL1 |  | 3x0332 | 4.21 | AI214 | 4.21 | 0 | 65535 |  |  |  | CCVM Cool Active power [kW]
| CVM Meter | Status | Standard | CCVMVoltageL2 |  | 3x0333 | 4.21 | AI215 | 4.21 | 0 | 5200 |  |  |  | CCVM Cool Phase L2 to neutral (N) voltage [V]
| CVM Meter | Status | Standard | CCVMCurrentL2 |  | 3x0334 | 4.21 | AI216 | 4.21 | 0 | 6000 |  |  |  | CVM Cool Current L2 value [A]
| CVM Meter | Status | Standard | CCVMActPowerL2 |  | 3x0335 | 4.21 | AI217 | 4.21 | 0 | 65535 |  |  |  | CCVM Cool Active power [kW]
| CVM Meter | Status | Standard | CCVMVoltageL3 |  | 3x0336 | 4.21 | AI218 | 4.21 | 0 | 5200 |  |  |  | CCVM Cool Phase L3 to neutral (N) voltage [V]
| CVM Meter | Status | Standard | CCVMCurrentL3 |  | 3x0337 | 4.21 | AI219 | 4.21 | 0 | 6000 |  |  |  | CCVM Cool Current L3 value [A]
| CVM Meter | Status | Standard | CCVMActPowerL3 |  | 3x0338 | 4.21 | AI220 | 4.21 | 0 | 65535 |  |  |  | CCVM Cool Active power [kW]
| CVM Meter | Status | Standard | CCVMActPowrIII |  | 3x0339 | 4.21 | AI221 | 4.21 | 0 | 65535 |  |  |  | CCVM Cool Active power three phases [W] (Low Byte)
| CVM Meter | Status | Standard | CCVMFrequency |  | 3x0340 | 4.21 | AI222 | 4.21 | 0 | 600 |  |  |  | CCVM Cool Frequency value [Hz]
| CVM Meter | Status | Standard | CCVMVoltagL1L2 |  | 3x0341 | 4.21 | AI223 | 4.21 | 0 | 5200 |  |  |  | CCVM Cool Phase-phase Voltage L1 to L2 [V]
| CVM Meter | Status | Standard | CCVMVoltagL2L3 |  | 3x0342 | 4.21 | AI224 | 4.21 | 0 | 5200 |  |  |  | CCVM Cool Phase-phase Voltage L2 to L3 [V]
| CVM Meter | Status | Standard | CCVMVoltagL3L1 |  | 3x0343 | 4.21 | AI225 | 4.21 | 0 | 5200 |  |  |  | CCVM Cool Phase-phase Voltage L3 to L1 [V]
| CVM Meter | Status | Standard | CCVMActEnergIII |  | 3x0344 | 4.26 | AI231 | 4.26 | 0 | 65535 |  |  |  | CCVM Cool Active energy three phases [kWh]
| CVM Meter | Status | Standard | CCVMCurrentL1H |  | 3x0345 | 5.07 | AI243 | 5.07 | 0 | 65535 |  |  |  | CCVM Current value [mA] - Note!: Values are calculated as (High byte) x 65536 + (Low byte) - High and low bytes = Integer
| CVM Meter | Status | Standard | CCVMActPoweL1H |  | 3x0346 | 5.07 | AI244 | 5.07 | 0 | 65535 |  |  |  | CCVM Active power [W] - Note!: Values are calculated as (High byte) x 65536 + (Low byte) - High and low bytes = Integer
| CVM Meter | Status | Standard | CCVMCurrentL2H |  | 3x0347 | 5.07 | AI245 | 5.07 | 0 | 65535 |  |  |  | CCVM Current value [mA] - Note!: Values are calculated as (High byte) x 65536 + (Low byte) - High and low bytes = Integer
| CVM Meter | Status | Standard | CCVMActPoweL2H |  | 3x0348 | 5.07 | AI246 | 5.07 | 0 | 65535 |  |  |  | CCVM Active power [W] - Note!: Values are calculated as (High byte) x 65536 + (Low byte) - High and low bytes = Integer
| CVM Meter | Status | Standard | CCVMCurrentL3H |  | 3x0349 | 5.07 | AI247 | 5.07 | 0 | 65535 |  |  |  | CCVM Current value [mA] - Note!: Values are calculated as (High byte) x 65536 + (Low byte) - High and low bytes = Integer
| CVM Meter | Status | Standard | CCVMActPoweL3H |  | 3x0350 | 5.07 | AI248 | 5.07 | 0 | 65535 |  |  |  | CCVM Active power [W] - Note!: Values are calculated as (High byte) x 65536 + (Low byte) - High and low bytes = Integer
| CVM Meter | Status | Standard | CCVMActPowIIIH |  | 3x0351 | 5.07 | AI249 | 5.07 | 0 | 65535 |  |  |  | CCVM Active power three phases [W] (High Byte) - Note!: Values are calculated as (High byte) x 65536 + (Low byte) - High and low bytes = Integer
| CVM Meter | Status | Standard | CCVMActEnrIIIH |  | 3x0352 | 5.07 | AI250 | 5.07 | 0 | 65535 |  |  |  | CCVM Active energy three phases [Wh] - Note!: Values are calculated as (High byte) x 65536 + (Low byte) - High and low bytes = Integer
| CVM Meter | Status | Standard | CVME3CKActEn3H |  | 3x0353 | 5.21 | AI255 | 5.21 | 0 | 65535 |  |  |  | CVM E3 Mini Active energy three phases [kWh] High byte - Note!: Values are calculated as (High byte) x 65536 + (Low byte) - High and low bytes = Integer
| CVM Meter | Status | Standard | CVME3CKActEn3 |  | 3x0354 | 5.21 | AI256 | 5.21 | 0 | 65535 |  |  |  | CVM E3 Mini Active energy three phases [kWh] Low byte - Note!: Values are calculated as (High byte) x 65536 + (Low byte) - High and low bytes = Integer
| CVM Meter | Status | Standard | CVME3CWActEn3H |  | 3x0355 | 5.21 | AI257 | 5.21 | 0 | 65535 |  |  |  | CVM E3 Mini Active energy three phases [Wh] High byte - Note!: Values are calculated as (High byte) x 65536 + (Low byte) - High and low bytes = Integer
| CVM Meter | Status | Standard | CVME3CWActEn3 |  | 3x0356 | 5.21 | AI258 | 5.21 | 0 | 65535 |  |  |  | CVM E3 Mini Active energy three phases [Wh] Low byte - Note!: Values are calculated as (High byte) x 65536 + (Low byte) - High and low bytes = Integer
| CVM Meter | Status | Standard | CCVME3CKActEn3H |  | 3x0357 | 5.21 | AI259 | 5.21 | 0 | 65535 |  |  |  | CCVM E3 Mini Active energy three phases [kWh] High byte - Note!: Values are calculated as (High byte) x 65536 + (Low byte) - High and low bytes = Integer
| CVM Meter | Status | Standard | CCVME3CKActEn3 |  | 3x0358 | 5.21 | AI260 | 5.21 | 0 | 65535 |  |  |  | CCVM E3 Mini Active energy three phases [kWh] Low byte - Note!: Values are calculated as (High byte) x 65536 + (Low byte) - High and low bytes = Integer
| CVM Meter | Status | Standard | CCVME3CWActEn3H |  | 3x0359 | 5.21 | AI261 | 5.21 | 0 | 65535 |  |  |  | CCVM E3 Mini Active energy three phases [Wh] High byte - Note!: Values are calculated as (High byte) x 65536 + (Low byte) - High and low bytes = Integer
| CVM Meter | Status | Standard | CCVME3CWActEn3 |  | 3x0360 | 5.21 | AI262 | 5.21 | 0 | 65535 |  |  |  | CCVM E3 Mini Active energy three phases [Wh] Low byte - Note!: Values are calculated as (High byte) x 65536 + (Low byte) - High and low bytes = Integer
| Heating coil, Electric | Status | Special | ElBattActPow |  | 3x0104 | 6.41 | AI226 | 4.21 | 0 | 30000 |  |  |  | Actual power (kW) electrical battery 1
| Heating coil, Electric | Status | Special | ElBatt2ActPow |  | 3x0105 | 6.41 | AI227 | 4.21 | 0 | 30000 |  |  |  | Actual power (kW) electrical battery 2
| Fan, supply | Status | Special | ECsupMtrPowOut |  | NA | NA | AI228 | 4.21 | 0 | 30000 |  |  |  | Actual power (kW) Supply fan
| Fan, extract | Status | Special | ECextMtrPowOut |  | NA | NA | AI229 | 4.21 | 0 | 30000 |  |  |  | Actual power (kW) Extract fan
| 1. Info | 1. Info | 1. Info | 1. Info |  | Holding register (R/W) |  | Analog value (R/W) | 1. Info | 1. Info | 1. Info | 1. Info |  |  | 1. Info
0x3000 | AHU controller | Set point |  | ManDriftMode |  | 4x0001 | x.xx | AV0 | x.xx | 0 | 7 | 0 | 0-Auto 1-ManStop 2-ManLo 3-ManHi 6-ManMed 7-AdvScheduler | 0-Auto 1-Manuel Stop 2-Manuel Lav 3-Manuel Høj 6-Manuel Medium 7-Kalender | 0=Auto 1=Manual stop 2=Manual low 3=Manual high 6=Manual medium 7=Calender
0x3440 | AHU controller | Set point |  | MtrRegMode |  | 4x0002 | x.xx | AV1 | x.xx | 0 | 12 | 0 | 0=pressure 1=flow 2=extract slave 3=supply slave 4=external V DC setpoint 5=fan optimizer supply/extract 6=fan optimizer with extract slave 7-Green Zone 8-Green Zone slave 9-Constant speed | 0-Tryk 1-Flow 2-fraluft Slave 3-tilluft Slave 4-Extern VDC Setpunkt 5 FAN-Optimizer tilluft/fraluft. 6 FAN-Optimizer med fraluft Slave 7-Green Zone 8-Green Zone slave 9-Konstant hast. | 0=pressure 1=flow 2=extract slave 3=supply slave 4=external V DC setpoint 5=fan optimizer supply/extract 6=fan optimizer with extract slave 7-Green Zone 8-Green Zone slave 9-Constant speed
0x3161 | Pressure | Set point |  | SupDuctPaLoSet | Pa | 4x0003 | x.xx | AV2 | x.xx | 0 | 2000 | 50 | LoSpeed DuctPressure Set [Pa] | Setpunkt for kanaltryk Lav tilluft [Pa] | Setpoint for duct pressure, low supply [Pa]
0x3162 | Pressure | Set point |  | SupDuctPaHiSet | Pa | 4x0004 | x.xx | AV3 | x.xx | 0 | 2000 | 200 | HiSpeed DuctPressure Set [Pa] | Setpunkt for kanaltryk Høj tilluft [Pa] | Setpoint for duct pressure, high supply [Pa]
0x3163 | Fan | Set point |  | SupDuctMinFlow | l/s | 4x0005 | x.xx | AV4 | x.xx | 0 | 30000 | 1500 | Supply Min Flow for DuctReg [l/s] | tilluft min. flow for kanal regulering [l/s] or [m3/h] or [CFM] (Depending on the unit selection in the OJ-Air2Master) | Min. supply duct flow [l/s] or [m3/h] or [CFM] (Depending on the unit selection in the OJ-Air2Master)
0x3164 | Fan | Set point |  | SupDuctMaxFlow | l/s | 4x0006 | x.xx | AV5 | x.xx | 0 | 30000 | 10000 | Supply Max Flow for DuctReg [l/s] | tilluft max. flow for kanal regulering [l/s] or [m3/h] or [CFM] (Depending on the unit selection in the OJ-Air2Master) | Max. supply duct flow P322
0x3261 | Pressure | Set point |  | ExtDuctPaLoSet | Pa | 4x0007 | x.xx | AV6 | x.xx | 0 | 2000 | 50 | LoSpeed DuctPressure Set [Pa] | Setpunkt for lav kanaltryk fraluft [Pa] | Setpoint for low duct pressure, extract [Pa]
0x3262 | Pressure | Set point |  | ExtDuctPaHiSet | Pa | 4x0008 | x.xx | AV7 | x.xx | 0 | 2000 | 200 | HiSpeed DuctPressure Set [Pa] | Setpunkt for høj kanaltryk fraluft [Pa] | Setpoint for high duct pressure, extract [Pa]
0x3263 | Fan | Set point |  | ExtDuctMinFlow | l/s | 4x0009 | x.xx | AV8 | x.xx | 0 | 30000 | 1500 | Extract Min Flow for DuctReg [l/s] | fraluft min. flow for kanalregulering [l/s] or [m3/h] or [CFM] (Depending on the unit selection in the OJ-Air2Master) | Min. extract duct flow [l/s] or [m3/h] or [CFM] (Depending on the unit selection in the OJ-Air2Master)
0x3264 | Fan | Set point |  | ExtDuctMaxFlow | l/s | 4x0010 | x.xx | AV9 | x.xx | 0 | 30000 | 10000 | Extract Max Flow for DuctReg [l/s] | fraluft Max. Flow for kanalregulering [l/s] or [m3/h] or [CFM] (Depending on the unit selection in the OJ-Air2Master) | Max. extract duct flow [l/s] or [m3/h] or [CFM] (Depending on the unit selection in the OJ-Air2Master)
0x3120 | Fan | Set point |  | SupLoSpeedSet | l/s | 4x0011 | x.xx | AV10 | x.xx | 0 | 30000 | 3000 | User SupplyFlow-LoSpeedSet [l/s] | Setpunkt tilluft flow-lav hastighed [l/s] or [m3/h] or [CFM] (Depending on the unit selection in the OJ-Air2Master) | Setpoint for supply flow, low speed [l/s] or [m3/h] or [CFM] (Depending on the unit selection in the OJ-Air2Master)
0x3121 | Fan | Set point |  | SupHiSpeedSet | l/s | 4x0012 | x.xx | AV11 | x.xx | 0 | 30000 | 7000 | User SupplyFlow-HiSpeedSet [l/s] | Setpunkt tilluft flow-høj hastighed [l/s] or [m3/h] or [CFM] (Depending on the unit selection in the OJ-Air2Master) | Setpoint for supply flow, high speed [l/s] or [m3/h] or [CFM] (Depending on the unit selection in the OJ-Air2Master)
0x3220 | Fan | Set point |  | ExtLoSpeedSet | l/s | 4x0014 | x.xx | AV12 | x.xx | 0 | 30000 | 3000 | User ExtractFlow-LoSpeedSet [l/s] | Setpunkt fraluft flow-lav hastighed [l/s] or [m3/h] or [CFM] (Depending on the unit selection in the OJ-Air2Master) | Setpoint for extract flow, low speed [l/s] or [m3/h] or [CFM] (Depending on the unit selection in the OJ-Air2Master)
0x3221 | Fan | Set point |  | ExtHiSpeedSet | l/s | 4x0015 | x.xx | AV13 | x.xx | 0 | 30000 | 7000 | User ExtractFlow-HiSpeedSet [l/s] | Setpunkt fraluft flow-høj hastighed [l/s] or [m3/h] or [CFM] (Depending on the unit selection in the OJ-Air2Master) | Setpoint for extract flow, high speed [l/s] or [m3/h] or [CFM] (Depending on the unit selection in the OJ-Air2Master)
0x3441 | Fan | Set point |  | MtrRegOffset | % | 4x0017 | x.xx | AV14 | x.xx | -5000 | 5000 | 0 | Offset for Sup/Ext Motor Slave and CO2 Reg [1/100%] | Offset for tilluft/fraluft Motor Slave og CO2 Reg [1/100%] | Supply/extract motor offset, slave and CO2 control [1/100%]
0x3441 | Fan | Set point |  | MtrRegOffset | % | NA | NA | AV15 | x.xx | -5000 | 5000 | 0 | Offset for Sup/Ext Motor Slave and CO2 Reg [1/100%] | Offset for tilluft/fraluft Motor Slave og CO2 Reg [1/100%] | Supply/extract motor offset, slave and CO2 control [1/100%]
0x3441 | Fan | Set point |  | MtrRegOffset | % | NA | NA | AV16 | x.xx | -5000 | 5000 | 0 | Offset for Sup/Ext Motor Slave and CO2 Reg [1/100%] | Offset for tilluft/fraluft Motor Slave og CO2 Reg [1/100%] | Supply/extract motor offset, slave and CO2 control [1/100%]
0x3450 | CO2 sensor | Set point |  | CO2_UserSetLP | ppm | 4x0020 | x.xx | AV17 | x.xx | 0 | 10000 | 1000 | CO2 Regulator User SetPoint for Lo timer Periode (HI CO2 Val) [ppm] | CO2 regulator Setpunkt for lav periode (HI CO2 Val) [ppm] | CO2 control: setpoint for low period (high CO2 value) [ppm]
0x3451 | CO2 sensor | Set point |  | CO2_UserSetHP | ppm | 4x0021 | x.xx | AV18 | x.xx | 0 | 10000 | 1000 | CO2 Regulator User SetPoint for Hi timer Periode(LO CO2 Val) [ppm] | CO2 regulator Setpunkt for høj periode (HI CO2 Val) [ppm] | CO2 control: setpoint for high period (high CO2 value) [ppm]
0x3456 | CO2 sensor | Set point |  | CO2_MinFlow | l/s | 4x0022 | x.xx | AV19 | x.xx | 0 | 30000 | 3000 | CO2 Regulator MinFlow [l/s] | CO2 regulator min. flow [l/s] or [m3/h] or [CFM] (Depending on the unit selection in the OJ-Air2Master) | CO2 control: min. flow [l/s] or [m3/h] or [CFM] (Depending on the unit selection in the OJ-Air2Master)
0x3457 | CO2 sensor | Set point |  | CO2_MaxFlow | l/s | 4x0023 | x.xx | AV20 | x.xx | 0 | 30000 | 7000 | CO2 Regulator MaxFlow [l/s] | CO2 regulator max. flow [l/s] or [m3/h] or [CFM] (Depending on the unit selection in the OJ-Air2Master) | CO2 control: max. flow [l/s] or [m3/h] or [CFM] (Depending on the unit selection in the OJ-Air2Master)
0x3458 | CO2 sensor | Set point |  | CO2_SupFlwOffs | % | 4x0024 | x.xx | AV21 | x.xx | -5000 | 5000 | 0 | CO2 Regulator SupFlow Offset [1/100%] | CO2 regulator tilluft flow offset [1/100%] | CO2 control: supply flow offset [1/100%]
0x3453 | CO2 sensor | Alarm |  | CO2_AlrLimit | ppm | 4x0025 | x.xx | AV22 | x.xx | 100 | 10000 | 2000 | CO2 ppm AlarmLimet Set [ppm] | CO2 ppm alarm grænse setpunkt [ppm] | CO2 concentration alarm limit setpoint [ppm]
0x3454 | CO2 sensor | Control |  | CO2_PB | ppm | 4x0026 | x.xx | AV23 | x.xx | 10 | 10000 | 500 | CO2 Regulator P-Band [ppm] | CO2 Regulator P-Bånd [ppm] | CO2 control: P-band [ppm]
0x3455 | CO2 sensor | Control | Standard | CO2_I_Time | sec | 4x0027 | x.xx | AV24 | x.xx | 10 | 30000 | 700 | CO2 Regulator I-Time [sec] | CO2 Regulator I-Tid [sec] | CO2 control: I-time [sec]
0x3470 | Fan optimizer | Set point |  | FAN_SupMinFlow | l/s | 4x0028 | x.xx | AV25 | x.xx | 0 | 30000 | 2000 | FAN-Opt Supply Regulator MinFlow [l/s] | FAN-Optimizer tilluft regulator Min. Flow [l/s] or [m3/h] or [CFM] (Depending on the unit selection in the OJ-Air2Master) | Fan optimizer supply control: min. flow [l/s] or [m3/h] or [CFM] (Depending on the unit selection in the OJ-Air2Master)
0x3471 | Fan optimizer | Set point |  | FAN_SupMaxFlow | l/s | 4x0029 | x.xx | AV26 | x.xx | 0 | 30000 | 10000 | FAN-Opt Supply Regulator MaxFlow [l/s] | FAN-Optimizer tilluft regulator MaxFlow [l/s] or [m3/h] or [CFM] (Depending on the unit selection in the OJ-Air2Master) | Fan optimizer extract control: min. flow [l/s] or [m3/h] or [CFM] (Depending on the unit selection in the OJ-Air2Master)
0x3472 | Fan optimizer | Set point |  | FAN_ExtMinFlow | l/s | 4x0030 | x.xx | AV27 | x.xx | 0 | 30000 | 2000 | FAN-Opt Extract Regulator MinFlow [l/s] | FAN-Optimizer fraluft regulator Min. Flow [l/s] or [m3/h] or [CFM] (Depending on the unit selection in the OJ-Air2Master) | Fan optimizer supply control: max. flow [l/s] or [m3/h] or [CFM] (Depending on the unit selection in the OJ-Air2Master)
0x3473 | Fan optimizer | Set point |  | FAN_ExtMaxFlow | l/s | 4x0031 | x.xx | AV28 | x.xx | 0 | 30000 | 10000 | FAN-Opt Extract Regulator MinFlow [l/s] | FAN-Optimizer fraluft regulator Max. Flow [l/s] or [m3/h] or [CFM] (Depending on the unit selection in the OJ-Air2Master) | Fan optimizer extract control: max. flow [l/s] or [m3/h] or [CFM] (Depending on the unit selection in the OJ-Air2Master)
0x3474 | Fan optimizer | Set point |  | FAN_ExtFlwOffs | % | 4x0032 | x.xx | AV29 | x.xx | -5000 | 5000 | 0 | FAN-Opt Regulator ExtFlow Offset [1/100%] | FAN-Optimizer regulator fraluft flow Offset G203 | Fan optimizer extract control: flow offset [1/100%]
0x3143 | Fan | Control | Standard | SupMtr_I_Time | sec | 4x0033 | x.xx | AV30 | x.xx | 5 | 1000 | 50 | Supply Motor Reg I-Time Set [Sec] | tilluft Motor Reg I-Tid Setpunkt [Sec] | Supply motor control: I-time setpoint [sec]
0x3243 | Fan | Control | Standard | ExtMtr_I_Time | sec | 4x0034 | x.xx | AV31 | x.xx | 5 | 1000 | 50 | Extract Motor Reg I-Time Set [Sec] | fraluft Motor Reg I-Tid Setpunkt [Sec] | Extract motor control: I-time setpoint [sec]
0x3122 | Fan | Fire |  | SupFlowFireSet | % | 4x0035 | x.xx | AV32 | x.xx | 0 | 10000 | 8000 | User Supply Motor Percent Set at Fire [%] | Setpunkt tilluft motor hastighed ved brandalarm [%] | Supply motor speed setpoint in case of fire alarm [%]
0x3222 | Fan | Fire |  | ExtFlowFireSet | % | 4x0036 | x.xx | AV33 | x.xx | 0 | 10000 | 8000 | User Extract Motor Percent Set at Fire [%] | Setpunkt fraluft motor hastighed ved brandalarm [%] | Extract motor speed setpoint in case of fire alarm [%]
0x3001 | Fan | Control |  | HS_AfterRunSet |  | 4x0037 | x.xx | AV34 | x.xx | 0 | 480 | 0 | HiSpeed Afterrun TimeSet [Min] | Efterløbstid høj hastighed [Min] | Run-on time, high speed [min]
0x33C0 | Fan | Set point |  | FlwTmpCmpSet | % | 4x0040 | x.xx | AV35 | x.xx | 0 | 5000 | 2500 | FlowOutTempComp PercentSet [1/100°C] | Reduktion af flow / Procent af Setpunkt [1/100°C] | Reduction of flow / percentage of setpoint [1/100%]
0x33C1 | Fan | Set point |  | FlwTmpCmpStart | °C | 4x0041 | x.xx | AV36 | x.xx | -1000 | 1500 | 500 | FlowOutTempComp StartTempSet [1/100°C] | Reduktion af flow / Start Temp. Setpunkt [1/100°C] | Reduction of flow / start temp. setpoint [1/100°C]
0x33C2 | Fan | Set point |  | FlwTmpCmpStop | °C | 4x0042 | x.xx | AV37 | x.xx | -3000 | -1000 | -2000 | FlowOutTempComp StopTempSet [1/100°C] | Reduktion af flow / Stop Temp. Setpunkt [1/100°C] | Reduction of flow / stop temp. setpoint [1/100°C]
0x3347 | Cooling, DX | Set point | Special | DXOutTempMin1 | °C | 4x0043 | x.xx | AV211 | x.xx | 0 | 4000 | 1600 | Min OutDoorTemp for CoolAgg. Relay 1 Active | Min. udetemperatur for aktivering DX relæ no. 1 | Min. outdoor temperature for activating DX relay no. 1
0x3348 | Cooling, DX | Set point | Special | DXOutTempMin2 | °C | 4x0044 | x.xx | AV212 | x.xx | 0 | 4000 | 1600 | Min OutDoorTemp for CoolAgg. Relay 2 Active | Min. udetemperatur for aktivering DX relæ no. 2 | Min. outdoor temperature for activating DX relay no. 2
0x3349 | Cooling, DX | Set point | Special | DXOutTempMin3 | °C | 4x0045 | x.xx | AV213 | x.xx | 0 | 4000 | 1600 | Min OutDoorTemp for CoolAgg. Relay 3 Active | Min. udetemperatur for aktivering DX relæ no. 3 | Min. outdoor temperature for activating DX relay no. 3
0x334A | Cooling, DX | Set point | Special | DXOutTempMin4 | °C | 4x0046 | x.xx | AV214 | x.xx | 0 | 4000 | 1600 | Min OutDoorTemp for CoolAgg. Relay 4 Active | Min. udetemperatur for aktivering DX relæ no. 4 | Min. outdoor temperature for activating DX relay no. 4
0x3800 | AHU controller | Time | Standard | TimeSw-Year |  | 4x0050 | x.xx | AV38 | x.xx | 2000 | 2099 |  | Current Year | Aktuel År | Actual year
0x3801 | AHU controller | Time | Standard | TimeSw-Month |  | 4x0051 | x.xx | AV39 | x.xx | 1 | 12 |  | Current Month | Aktuel Måned | Actual month
0x3802 | AHU controller | Time | Standard | TimeSw-Date |  | 4x0052 | x.xx | AV40 | x.xx | 1 | 31 |  | Current Day | Aktuel Dato | Actual date
0x3803 | AHU controller | Time | Standard | TimeSw-Hour | h | 4x0053 | x.xx | AV41 | x.xx | 0 | 23 |  | Current Hour | Aktuel Time | Actual hour
0x3804 | AHU controller | Time | Standard | TimeSw-Minute | Min | 4x0054 | x.xx | AV42 | x.xx | 0 | 59 |  | Current Minute | Aktuel Minutter | Actual minutes
0x3805 | AHU controller | Time | Standard | TimeSw-Second | Sec | 4x0055 | x.xx | AV43 | x.xx | 0 | 59 |  | Current Second | Aktuel Sekunder | Actual seconds
0x3808 | AHU controller | Control |  | ExtDrfStartDay |  | 4x0056 | x.xx | AV44 | x.xx | 0 | 6 | 0 | Extended Drift Stop Day (0-Mon..6-Sun) | Forlænget Drift Start - Dag (0-Man..6-Søn) | Extended operation start – day (0=Mon..6=Sun)
0x3809 | AHU controller | Control |  | ExtDrfStartMin | Min | 4x0057 | x.xx | AV45 | x.xx | 0 | 1439 | 0 | Extended Drift Stop Minute (Hour*60+Min) | Forlænget Drift Start - Minut (Timer*60+Min) | Extended operation start – time (hours times 60 plus minutes)
0x380A | AHU controller | Control |  | ExtDrfStopDay |  | 4x0058 | x.xx | AV46 | x.xx | 0 | 6 | 0 | Extended Drift Stop Day (0-Mon..6-Sun) | Forlænget Drift Stop - Dag (0-Man..6-Søn) | Extended operation stop – day (0=Mon..6=Sun)
0x380B | AHU controller | Control |  | ExtDrfStopMin | Min | 4x0059 | x.xx | AV47 | x.xx | 0 | 1439 | 0 | Extended Drift Stop Minute (Hour*60+Min) | Forlænget Drift Stop - Minut (Timer*60+Min) | Extended operation stop – time (hours times 60 plus minutes)
0x3870 | AHU controller | Week Schedule | Standard | TimeSw-DayMode |  | 4x0060 | x.xx | AV48 | x.xx | 0 | 2 | 0 | DayMode (0..2)0-Mon..Sun, 1-Mon..Fri+Weekend, 2-Week | Tidsprogram Type (0..2) 0-Man..Søn, 1-Man..Fre+Weekend, 2-Uge | Timer program type (0..2) 0=Mon..Sun, 1=Mon..Fri+weekend, 2=all week
0x3810 | AHU controller | Week Schedule | Standard | TimeSw-Start00 | Min | 4x0061 | x.xx | AV49 | x.xx | 0 | 1439 | 480 | StartTime for TimeSwitch Zone00 [Minute] | Mandag start 1. tidsperiode [Minutter fra midnat] | Monday: First period start time [minutes after midnight]
0x3811 | AHU controller | Week Schedule | Standard | TimeSw-Start01 | Min | 4x0062 | x.xx | AV50 | x.xx | 0 | 1439 | 960 | StartTime for TimeSwitch Zone01 [Minute] | Tirsdag start 1. tidsperiode [Minutter fra midnat] | Tuesday: First period start time [minutes after midnight]
0x3812 | AHU controller | Week Schedule | Standard | TimeSw-Start02 | Min | 4x0063 | x.xx | AV51 | x.xx | 0 | 1439 | 360 | StartTime for TimeSwitch Zone02 [Minute] | Onsdag start 1. tidsperiode [Minutter fra midnat] | Wednesday: First period start time [minutes after midnight]
0x3813 | AHU controller | Week Schedule | Standard | TimeSw-Start03 | Min | 4x0064 | x.xx | AV52 | x.xx | 0 | 1439 | 0 | StartTime for TimeSwitch Zone03 [Minute] | Torsdag start 1. tidsperiode [Minutter fra midnat] | Thursday: First period start time [minutes after midnight]
0x3814 | AHU controller | Week Schedule | Standard | TimeSw-Start04 | Min | 4x0065 | x.xx | AV53 | x.xx | 0 | 1439 | 480 | StartTime for TimeSwitch Zone04 [Minute] | Fredag start 1. tidsperiode [Minutter fra midnat] | Friday: First period start time [minutes after midnight]
0x3815 | AHU controller | Week Schedule | Standard | TimeSw-Start05 | Min | 4x0066 | x.xx | AV54 | x.xx | 0 | 1439 | 960 | StartTime for TimeSwitch Zone05 [Minute] | Lørdag start 1. tidsperiode [Minutter fra midnat] | Saturday: First period start time [minutes after midnight]
0x3816 | AHU controller | Week Schedule | Standard | TimeSw-Start06 | Min | 4x0067 | x.xx | AV55 | x.xx | 0 | 1439 | 360 | StartTime for TimeSwitch Zone06 [Minute] | Søndag start 1. tidsperiode [Minutter fra midnat] | Sunday: First period start time [minutes after midnight]
0x3817 | AHU controller | Week Schedule | Standard | TimeSw-Start07 | Min | 4x0068 | x.xx | AV56 | x.xx | 0 | 1439 | 0 | StartTime for TimeSwitch Zone07 [Minute] | Mandag start 2. tidsperiode [Minutter fra midnat] | Monday: Second period start time [minutes after midnight]
0x3818 | AHU controller | Week Schedule | Standard | TimeSw-Start08 | Min | 4x0069 | x.xx | AV57 | x.xx | 0 | 1439 | 480 | StartTime for TimeSwitch Zone08 [Minute] | Tirsdag start 2. tidsperiode [Minutter fra midnat] | Tuesday: Second period start time [minutes after midnight]
0x3819 | AHU controller | Week Schedule | Standard | TimeSw-Start09 | Min | 4x0070 | x.xx | AV58 | x.xx | 0 | 1439 | 960 | StartTime for TimeSwitch Zone09 [Minute] | Onsdag start 2. tidsperiode [Minutter fra midnat] | Wednesday: Second period start time [minutes after midnight]
0x381A | AHU controller | Week Schedule | Standard | TimeSw-Start10 | Min | 4x0071 | x.xx | AV59 | x.xx | 0 | 1439 | 360 | StartTime for TimeSwitch Zone10 [Minute] | Torsdag start 2. tidsperiode [Minutter fra midnat] | Thursday: Second period start time [minutes after midnight]
0x381B | AHU controller | Week Schedule | Standard | TimeSw-Start11 | Min | 4x0072 | x.xx | AV60 | x.xx | 0 | 1439 | 0 | StartTime for TimeSwitch Zone11 [Minute] | Fredag start 2. tidsperiode [Minutter fra midnat] | Friday: Second period start time [minutes after midnight]
0x381C | AHU controller | Week Schedule | Standard | TimeSw-Start12 | Min | 4x0073 | x.xx | AV61 | x.xx | 0 | 1439 | 480 | StartTime for TimeSwitch Zone12 [Minute] | Lørdag start 2. tidsperiode [Minutter fra midnat] | Saturday: Second period start time [minutes after midnight]
0x381D | AHU controller | Week Schedule | Standard | TimeSw-Start13 | Min | 4x0074 | x.xx | AV62 | x.xx | 0 | 1439 | 960 | StartTime for TimeSwitch Zone13 [Minute] | Søndag start 2. tidsperiode [Minutter fra midnat] | Sunday: Second period start time [minutes after midnight]
0x381E | AHU controller | Week Schedule | Standard | TimeSw-Start14 | Min | 4x0075 | x.xx | AV63 | x.xx | 0 | 1439 | 360 | StartTime for TimeSwitch Zone14 [Minute] | Mandag start 3. tidsperiode [Minutter fra midnat] | Monday: Third period start time [minutes after midnight]
0x381F | AHU controller | Week Schedule | Standard | TimeSw-Start15 | Min | 4x0076 | x.xx | AV64 | x.xx | 0 | 1439 | 0 | StartTime for TimeSwitch Zone15 [Minute] | Tirsdag start 3. tidsperiode [Minutter fra midnat] | Tuesday: Third period start time [minutes after midnight]
0x3820 | AHU controller | Week Schedule | Standard | TimeSw-Start16 | Min | 4x0077 | x.xx | AV65 | x.xx | 0 | 1439 | 480 | StartTime for TimeSwitch Zone16 [Minute] | Onsdag start 3. tidsperiode [Minutter fra midnat] | Wednesday: Third period start time [minutes after midnight]
0x3821 | AHU controller | Week Schedule | Standard | TimeSw-Start17 | Min | 4x0078 | x.xx | AV66 | x.xx | 0 | 1439 | 960 | StartTime for TimeSwitch Zone17 [Minute] | Torsdag start 3. tidsperiode [Minutter fra midnat] | Thursday: Third period start time [minutes after midnight]
0x3822 | AHU controller | Week Schedule | Standard | TimeSw-Start18 | Min | 4x0079 | x.xx | AV67 | x.xx | 0 | 1439 | 360 | StartTime for TimeSwitch Zone18 [Minute] | Fredag start 3. tidsperiode [Minutter fra midnat] | Friday: Third period start time [minutes after midnight]
0x3823 | AHU controller | Week Schedule | Standard | TimeSw-Start19 | Min | 4x0080 | x.xx | AV68 | x.xx | 0 | 1439 | 0 | StartTime for TimeSwitch Zone19 [Minute] | Lørdag start 3. tidsperiode [Minutter fra midnat] | Saturday: Third period start time [minutes after midnight]
0x3824 | AHU controller | Week Schedule | Standard | TimeSw-Start20 | Min | 4x0081 | x.xx | AV69 | x.xx | 0 | 1439 | 480 | StartTime for TimeSwitch Zone20 [Minute] | Søndag start 3. tidsperiode [Minutter fra midnat] | Sunday: Third period start time [minutes after midnight]
0x3825 | AHU controller | Week Schedule | Standard | TimeSw-Start21 | Min | 4x0082 | x.xx | AV70 | x.xx | 0 | 1439 | 960 | StartTime for TimeSwitch Zone21 [Minute] | Mandag start 4. tidsperiode [Minutter fra midnat] | Monday: Fourth period start time [minutes after midnight]
0x3826 | AHU controller | Week Schedule | Standard | TimeSw-Start22 | Min | 4x0083 | x.xx | AV71 | x.xx | 0 | 1439 | 360 | StartTime for TimeSwitch Zone22 [Minute] | Tirsdag start 4. tidsperiode [Minutter fra midnat] | Tuesday: Fourth period start time [minutes after midnight]
0x3827 | AHU controller | Week Schedule | Standard | TimeSw-Start23 | Min | 4x0084 | x.xx | AV72 | x.xx | 0 | 1439 | 0 | StartTime for TimeSwitch Zone23 [Minute] | Onsdag start 4. tidsperiode [Minutter fra midnat] | Wednesday: Fourth period start time [minutes after midnight]
0x3828 | AHU controller | Week Schedule | Standard | TimeSw-Start24 | Min | 4x0085 | x.xx | AV73 | x.xx | 0 | 1439 | 480 | StartTime for TimeSwitch Zone24 [Minute] | Torsdag start 4. tidsperiode [Minutter fra midnat] | Thursday: Fourth period start time [minutes after midnight]
0x3829 | AHU controller | Week Schedule | Standard | TimeSw-Start25 | Min | 4x0086 | x.xx | AV74 | x.xx | 0 | 1439 | 960 | StartTime for TimeSwitch Zone25 [Minute] | Fredag start 4. tidsperiode [Minutter fra midnat] | Friday: Fourth period start time [minutes after midnight]
0x382A | AHU controller | Week Schedule | Standard | TimeSw-Start26 | Min | 4x0087 | x.xx | AV75 | x.xx | 0 | 1439 | 360 | StartTime for TimeSwitch Zone26 [Minute] | Lørdag start 4. tidsperiode [Minutter fra midnat] | Saturday: Fourth period start time [minutes after midnight]
0x382B | AHU controller | Week Schedule | Standard | TimeSw-Start27 | Min | 4x0088 | x.xx | AV76 | x.xx | 0 | 1439 | 0 | StartTime for TimeSwitch Zone27 [Minute] | Søndag start 4. tidsperiode [Minutter fra midnat] | Sunday: Fourth period start time [minutes after midnight]
0x3830 | AHU controller | Week Schedule | Standard | TimeSw-Stop00 | Min | 4x0089 | x.xx | AV77 | x.xx | 1 | 1440 | 960 | StopTime for TimeSwitch Zone00 [Minute] | Mandag stop 1. tidsperiode [Minutter fra midnat] | Monday: First period stop time [minutes after midnight]
0x3831 | AHU controller | Week Schedule | Standard | TimeSw-Stop01 | Min | 4x0090 | x.xx | AV78 | x.xx | 1 | 1440 | 1440 | StopTime for TimeSwitch Zone01 [Minute] | Tirsdag stop 1. tidsperiode [Minutter fra midnat] | Tuesday: First period stop time [minutes after midnight]
0x3832 | AHU controller | Week Schedule | Standard | TimeSw-Stop02 | Min | 4x0091 | x.xx | AV79 | x.xx | 1 | 1440 | 480 | StopTime for TimeSwitch Zone02 [Minute] | Onsdag stop 1. tidsperiode [Minutter fra midnat] | Wednesday: First period stop time [minutes after midnight]
0x3833 | AHU controller | Week Schedule | Standard | TimeSw-Stop03 | Min | 4x0092 | x.xx | AV80 | x.xx | 1 | 1440 | 360 | StopTime for TimeSwitch Zone03 [Minute] | Torsdag stop 1. tidsperiode [Minutter fra midnat] | Thursday: First period stop time [minutes after midnight]
0x3834 | AHU controller | Week Schedule | Standard | TimeSw-Stop04 | Min | 4x0093 | x.xx | AV81 | x.xx | 1 | 1440 | 960 | StopTime for TimeSwitch Zone04 [Minute] | Fredag stop 1. tidsperiode [Minutter fra midnat] | Friday: First period stop time [minutes after midnight]
0x3835 | AHU controller | Week Schedule | Standard | TimeSw-Stop05 | Min | 4x0094 | x.xx | AV82 | x.xx | 1 | 1440 | 1440 | StopTime for TimeSwitch Zone05 [Minute] | Lørdag stop 1. tidsperiode [Minutter fra midnat] | Saturday: First period stop time [minutes after midnight]
0x3836 | AHU controller | Week Schedule | Standard | TimeSw-Stop06 | Min | 4x0095 | x.xx | AV83 | x.xx | 1 | 1440 | 480 | StopTime for TimeSwitch Zone06 [Minute] | Søndag stop 1. tidsperiode [Minutter fra midnat] | Sunday: First period stop time [minutes after midnight]
0x3837 | AHU controller | Week Schedule | Standard | TimeSw-Stop07 | Min | 4x0096 | x.xx | AV84 | x.xx | 1 | 1440 | 360 | StopTime for TimeSwitch Zone07 [Minute] | Mandag stop 2. tidsperiode [Minutter fra midnat] | Monday: Second period stop time [minutes after midnight]
0x3838 | AHU controller | Week Schedule | Standard | TimeSw-Stop08 | Min | 4x0097 | x.xx | AV85 | x.xx | 1 | 1440 | 960 | StopTime for TimeSwitch Zone08 [Minute] | Tirsdag stop 2. tidsperiode [Minutter fra midnat] | Tuesday: Second period stop time [minutes after midnight]
0x3839 | AHU controller | Week Schedule | Standard | TimeSw-Stop09 | Min | 4x0098 | x.xx | AV86 | x.xx | 1 | 1440 | 1440 | StopTime for TimeSwitch Zone09 [Minute] | Onsdag stop 2. tidsperiode [Minutter fra midnat] | Wednesday: Second period stop time [minutes after midnight]
0x383A | AHU controller | Week Schedule | Standard | TimeSw-Stop10 | Min | 4x0099 | x.xx | AV87 | x.xx | 1 | 1440 | 480 | StopTime for TimeSwitch Zone10 [Minute] | Torsdag stop 2. tidsperiode [Minutter fra midnat] | Thursday: Second period stop time [minutes after midnight]
0x383B | AHU controller | Week Schedule | Standard | TimeSw-Stop11 | Min | 4x0100 | x.xx | AV88 | x.xx | 1 | 1440 | 360 | StopTime for TimeSwitch Zone11 [Minute] | Fredag stop 2. tidsperiode [Minutter fra midnat] | Friday: Second period stop time [minutes after midnight]
0x383C | AHU controller | Week Schedule | Standard | TimeSw-Stop12 | Min | 4x0101 | x.xx | AV89 | x.xx | 1 | 1440 | 960 | StopTime for TimeSwitch Zone12 [Minute] | Lørdag stop 2. tidsperiode [Minutter fra midnat] | Saturday: Second period stop time [minutes after midnight]
0x383D | AHU controller | Week Schedule | Standard | TimeSw-Stop13 | Min | 4x0102 | x.xx | AV90 | x.xx | 1 | 1440 | 1440 | StopTime for TimeSwitch Zone13 [Minute] | Søndag stop 2. tidsperiode [Minutter fra midnat] | Sunday: Second period stop time [minutes after midnight]
0x383E | AHU controller | Week Schedule | Standard | TimeSw-Stop14 | Min | 4x0103 | x.xx | AV91 | x.xx | 1 | 1440 | 480 | StopTime for TimeSwitch Zone14 [Minute] | Mandag stop 3. tidsperiode [Minutter fra midnat] | Monday: Third period stop time [minutes after midnight]
0x383F | AHU controller | Week Schedule | Standard | TimeSw-Stop15 | Min | 4x0104 | x.xx | AV92 | x.xx | 1 | 1440 | 360 | StopTime for TimeSwitch Zone15 [Minute] | Tirsdag stop 3. tidsperiode [Minutter fra midnat] | Tuesday: Third period stop time [minutes after midnight]
0x3840 | AHU controller | Week Schedule | Standard | TimeSw-Stop16 | Min | 4x0105 | x.xx | AV93 | x.xx | 1 | 1440 | 960 | StopTime for TimeSwitch Zone16 [Minute] | Onsdag stop 3. tidsperiode [Minutter fra midnat] | Wednesday: Third period stop time [minutes after midnight]
0x3841 | AHU controller | Week Schedule | Standard | TimeSw-Stop17 | Min | 4x0106 | x.xx | AV94 | x.xx | 1 | 1440 | 1440 | StopTime for TimeSwitch Zone17 [Minute] | Torsdag stop 3. tidsperiode [Minutter fra midnat] | Thursday: Third period stop time [minutes after midnight]
0x3842 | AHU controller | Week Schedule | Standard | TimeSw-Stop18 | Min | 4x0107 | x.xx | AV95 | x.xx | 1 | 1440 | 480 | StopTime for TimeSwitch Zone18 [Minute] | Fredag stop 3. tidsperiode [Minutter fra midnat] | Friday: Third period stop time [minutes after midnight]
0x3843 | AHU controller | Week Schedule | Standard | TimeSw-Stop19 | Min | 4x0108 | x.xx | AV96 | x.xx | 1 | 1440 | 360 | StopTime for TimeSwitch Zone19 [Minute] | Lørdag stop 3. tidsperiode [Minutter fra midnat] | Saturday: Third period stop time [minutes after midnight]
0x3844 | AHU controller | Week Schedule | Standard | TimeSw-Stop20 | Min | 4x0109 | x.xx | AV97 | x.xx | 1 | 1440 | 960 | StopTime for TimeSwitch Zone20 [Minute] | Søndag stop 3. tidsperiode [Minutter fra midnat] | Sunday: Third period stop time [minutes after midnight]
0x3845 | AHU controller | Week Schedule | Standard | TimeSw-Stop21 | Min | 4x0110 | x.xx | AV98 | x.xx | 1 | 1440 | 1440 | StopTime for TimeSwitch Zone21 [Minute] | Mandag stop 4. tidsperiode [Minutter fra midnat] | Monday: Fourth period stop time [minutes after midnight]
0x3846 | AHU controller | Week Schedule | Standard | TimeSw-Stop22 | Min | 4x0111 | x.xx | AV99 | x.xx | 1 | 1440 | 480 | StopTime for TimeSwitch Zone22 [Minute] | Tirsdag stop 4. tidsperiode [Minutter fra midnat] | Tuesday: Fourth period stop time [minutes after midnight]
0x3847 | AHU controller | Week Schedule | Standard | TimeSw-Stop23 | Min | 4x0112 | x.xx | AV100 | x.xx | 1 | 1440 | 360 | StopTime for TimeSwitch Zone23 [Minute] | Onsdag stop 4. tidsperiode [Minutter fra midnat] | Wednesday: Fourth period stop time [minutes after midnight]
0x3848 | AHU controller | Week Schedule | Standard | TimeSw-Stop24 | Min | 4x0113 | x.xx | AV101 | x.xx | 1 | 1440 | 960 | StopTime for TimeSwitch Zone24 [Minute] | Torsdag stop 4. tidsperiode [Minutter fra midnat] | Thursday: Fourth period stop time [minutes after midnight]
0x3849 | AHU controller | Week Schedule | Standard | TimeSw-Stop25 | Min | 4x0114 | x.xx | AV102 | x.xx | 1 | 1440 | 1440 | StopTime for TimeSwitch Zone25 [Minute] | Fredag stop 4. tidsperiode [Minutter fra midnat] | Friday: Fourth period stop time [minutes after midnight]
0x384A | AHU controller | Week Schedule | Standard | TimeSw-Stop26 | Min | 4x0115 | x.xx | AV103 | x.xx | 1 | 1440 | 480 | StopTime for TimeSwitch Zone26 [Minute] | Lørdag stop 4. tidsperiode [Minutter fra midnat] | Saturday: Fourth period stop time [minutes after midnight]
0x384B | AHU controller | Week Schedule | Standard | TimeSw-Stop27 | Min | 4x0116 | x.xx | AV104 | x.xx | 1 | 1440 | 360 | StopTime for TimeSwitch Zone27 [Minute] | Søndag stop 4. tidsperiode [Minutter fra midnat] | Sunday: Fourth period stop time [minutes after midnight]
0x3850 | AHU controller | Week Schedule | Standard | TimeSw-Mode00 |  | 4x0117 | x.xx | AV105 | x.xx | 0 | 6 | 2 | Mode Zone00 0-OFF, 1-LoSpeed, 2-HiSpeed, 6-MedSpeed | Mandag 1.tidsperiode. Drift Tilstand. 0-OFF, 1-Lav Hastighed, 2-Høj Hastighed, 6-Medium Hastighed | Monday: First period operating mode: 0=OFF, 1=low speed, 2=high speed, 6=medium speed
0x3851 | AHU controller | Week Schedule | Standard | TimeSw-Mode01 |  | 4x0118 | x.xx | AV106 | x.xx | 0 | 6 | 1 | Mode Zone01 0-OFF, 1-LoSpeed, 2-HiSpeed, 6-MedSpeed | Tirsdag 1.tidsperiode. Drift Tilstand. 0-OFF, 1-Lav Hastighed, 2-Høj Hastighed, 6-Medium Hastighed | Tuesday: First period operating mode: 0=OFF, 1=low speed, 2=high speed , 6=medium speed
0x3852 | AHU controller | Week Schedule | Standard | TimeSw-Mode02 |  | 4x0119 | x.xx | AV107 | x.xx | 0 | 6 | 1 | Mode Zone02 0-OFF, 1-LoSpeed, 2-HiSpeed, 6-MedSpeed | Onsdag 1.tidsperiode. Drift Tilstand. 0-OFF, 1-Lav Hastighed, 2-Høj Hastighed, 6-Medium Hastighed | Wednesday: First period operating mode: 0=OFF, 1=low speed, 2=high speed , 6=medium speed
0x3853 | AHU controller | Week Schedule | Standard | TimeSw-Mode03 |  | 4x0120 | x.xx | AV108 | x.xx | 0 | 6 | 0 | Mode Zone03 0-OFF, 1-LoSpeed, 2-HiSpeed, 6-MedSpeed | Torsdag 1.tidsperiode. Drift Tilstand. 0-OFF, 1-Lav Hastighed, 2-Høj Hastighed, 6-Medium Hastighed | Thursday: First period operating mode: 0=OFF, 1=low speed, 2=high speed , 6=medium speed
0x3854 | AHU controller | Week Schedule | Standard | TimeSw-Mode04 |  | 4x0121 | x.xx | AV109 | x.xx | 0 | 6 | 2 | Mode Zone04 0-OFF, 1-LoSpeed, 2-HiSpeed, 6-MedSpeed | Fredag 1.tidsperiode. Drift Tilstand. 0-OFF, 1-Lav Hastighed, 2-Høj Hastighed, 6-Medium Hastighed | Friday: First period operating mode: 0=OFF, 1=low speed, 2=high speed , 6=medium speed
0x3855 | AHU controller | Week Schedule | Standard | TimeSw-Mode05 |  | 4x0122 | x.xx | AV110 | x.xx | 0 | 6 | 1 | Mode Zone05 0-OFF, 1-LoSpeed, 2-HiSpeed, 6-MedSpeed | Lørdag 1.tidsperiode. Drift Tilstand. 0-OFF, 1-Lav Hastighed, 2-Høj Hastighed, 6-Medium Hastighed | Saturday: First period operating mode: 0=OFF, 1=low speed, 2=high speed , 6=medium speed
0x3856 | AHU controller | Week Schedule | Standard | TimeSw-Mode06 |  | 4x0123 | x.xx | AV111 | x.xx | 0 | 6 | 1 | Mode Zone06 0-OFF, 1-LoSpeed, 2-HiSpeed, 6-MedSpeed | Søndag 1.tidsperiode. Drift Tilstand. 0-OFF, 1-Lav Hastighed, 2-Høj Hastighed, 6-Medium Hastighed | Sunday: First period operating mode: 0=OFF, 1=low speed, 2=high speed , 6=medium speed
0x3857 | AHU controller | Week Schedule | Standard | TimeSw-Mode07 |  | 4x0124 | x.xx | AV112 | x.xx | 0 | 6 | 0 | Mode Zone07 0-OFF, 1-LoSpeed, 2-HiSpeed, 6-MedSpeed | Mandag 2.tidsperiode. Drift Tilstand. 0-OFF, 1-Lav Hastighed, 2-Høj Hastighed, 6-Medium Hastighed | Monday: Second period operating mode: 0=OFF, 1=low speed, 2=high speed , 6=medium speed
0x3858 | AHU controller | Week Schedule | Standard | TimeSw-Mode08 |  | 4x0125 | x.xx | AV113 | x.xx | 0 | 6 | 2 | Mode Zone08 0-OFF, 1-LoSpeed, 2-HiSpeed, 6-MedSpeed | Tirsdag 2.tidsperiode. Drift Tilstand. 0-OFF, 1-Lav Hastighed, 2-Høj Hastighed, 6-Medium Hastighed | Tuesday: Second period operating mode: 0=OFF, 1=low speed, 2=high speed , 6=medium speed
0x3859 | AHU controller | Week Schedule | Standard | TimeSw-Mode09 |  | 4x0126 | x.xx | AV114 | x.xx | 0 | 6 | 1 | Mode Zone09 0-OFF, 1-LoSpeed, 2-HiSpeed, 6-MedSpeed | Onsdag 2.tidsperiode. Drift Tilstand. 0-OFF, 1-Lav Hastighed, 2-Høj Hastighed, 6-Medium Hastighed | Wednesday: Second period operating mode: 0=OFF, 1=low speed, 2=high speed , 6=medium speed
0x385A | AHU controller | Week Schedule | Standard | TimeSw-Mode10 |  | 4x0127 | x.xx | AV115 | x.xx | 0 | 6 | 1 | Mode Zone10 0-OFF, 1-LoSpeed, 2-HiSpeed, 6-MedSpeed | Torsdag 2.tidsperiode. Drift Tilstand. 0-OFF, 1-Lav Hastighed, 2-Høj Hastighed, 6-Medium Hastighed | Thursday: Second period operating mode: 0=OFF, 1=low speed, 2=high speed , 6=medium speed
0x385B | AHU controller | Week Schedule | Standard | TimeSw-Mode11 |  | 4x0128 | x.xx | AV116 | x.xx | 0 | 6 | 0 | Mode Zone11 0-OFF, 1-LoSpeed, 2-HiSpeed, 6-MedSpeed | Fredag 2.tidsperiode. Drift Tilstand. 0-OFF, 1-Lav Hastighed, 2-Høj Hastighed, 6-Medium Hastighed | Friday: Second period operating mode: 0=OFF, 1=low speed, 2=high speed , 6=medium speed
0x385C | AHU controller | Week Schedule | Standard | TimeSw-Mode12 |  | 4x0129 | x.xx | AV117 | x.xx | 0 | 6 | 2 | Mode Zone12 0-OFF, 1-LoSpeed, 2-HiSpeed, 6-MedSpeed | Lørdag 2.tidsperiode. Drift Tilstand. 0-OFF, 1-Lav Hastighed, 2-Høj Hastighed, 6-Medium Hastighed | Saturday: Second period operating mode: 0=OFF, 1=low speed, 2=high speed , 6=medium speed
0x385D | AHU controller | Week Schedule | Standard | TimeSw-Mode13 |  | 4x0130 | x.xx | AV118 | x.xx | 0 | 6 | 1 | Mode Zone13 0-OFF, 1-LoSpeed, 2-HiSpeed, 6-MedSpeed | Søndag 2.tidsperiode. Drift Tilstand. 0-OFF, 1-Lav Hastighed, 2-Høj Hastighed, 6-Medium Hastighed | Sunday: Second period operating mode: 0=OFF, 1=low speed, 2=high speed , 6=medium speed
0x385E | AHU controller | Week Schedule | Standard | TimeSw-Mode14 |  | 4x0131 | x.xx | AV119 | x.xx | 0 | 6 | 1 | Mode Zone14 0-OFF, 1-LoSpeed, 2-HiSpeed, 6-MedSpeed | Mandag 3.tidsperiode. Drift Tilstand. 0-OFF, 1-Lav Hastighed, 2-Høj Hastighed, 6-Medium Hastighed | Monday: Third period operating mode: 0=OFF, 1=low speed, 2=high speed , 6=medium speed
0x385F | AHU controller | Week Schedule | Standard | TimeSw-Mode15 |  | 4x0132 | x.xx | AV120 | x.xx | 0 | 6 | 0 | Mode Zone15 0-OFF, 1-LoSpeed, 2-HiSpeed, 6-MedSpeed | Tirsdag 3.tidsperiode. Drift Tilstand. 0-OFF, 1-Lav Hastighed, 2-Høj Hastighed, 6-Medium Hastighed | Tuesday: Third period operating mode: 0=OFF, 1=low speed, 2=high speed , 6=medium speed
0x3860 | AHU controller | Week Schedule | Standard | TimeSw-Mode16 |  | 4x0133 | x.xx | AV121 | x.xx | 0 | 6 | 2 | Mode Zone16 0-OFF, 1-LoSpeed, 2-HiSpeed, 6-MedSpeed | Onsdag 3.tidsperiode. Drift Tilstand. 0-OFF, 1-Lav Hastighed, 2-Høj Hastighed, 6-Medium Hastighed | Wednesday: Third period operating mode: 0=OFF, 1=low speed, 2=high speed , 6=medium speed
0x3861 | AHU controller | Week Schedule | Standard | TimeSw-Mode17 |  | 4x0134 | x.xx | AV122 | x.xx | 0 | 6 | 1 | Mode Zone17 0-OFF, 1-LoSpeed, 2-HiSpeed, 6-MedSpeed | Torsdag 3.tidsperiode. Drift Tilstand. 0-OFF, 1-Lav Hastighed, 2-Høj Hastighed, 6-Medium Hastighed | Thursday: Third period operating mode: 0=OFF, 1=low speed, 2=high speed , 6=medium speed
0x3862 | AHU controller | Week Schedule | Standard | TimeSw-Mode18 |  | 4x0135 | x.xx | AV123 | x.xx | 0 | 6 | 1 | Mode Zone18 0-OFF, 1-LoSpeed, 2-HiSpeed, 6-MedSpeed | Fredag 3.tidsperiode. Drift Tilstand. 0-OFF, 1-Lav Hastighed, 2-Høj Hastighed, 6-Medium Hastighed | Friday: Third period operating mode: 0=OFF, 1=low speed, 2=high speed , 6=medium speed
0x3863 | AHU controller | Week Schedule | Standard | TimeSw-Mode19 |  | 4x0136 | x.xx | AV124 | x.xx | 0 | 6 | 0 | Mode Zone19 0-OFF, 1-LoSpeed, 2-HiSpeed, 6-MedSpeed | Lørdag 3.tidsperiode. Drift Tilstand. 0-OFF, 1-Lav Hastighed, 2-Høj Hastighed, 6-Medium Hastighed | Saturday: Third period operating mode: 0=OFF, 1=low speed, 2=high speed , 6=medium speed
0x3864 | AHU controller | Week Schedule | Standard | TimeSw-Mode20 |  | 4x0137 | x.xx | AV125 | x.xx | 0 | 6 | 2 | Mode Zone20 0-OFF, 1-LoSpeed, 2-HiSpeed, 6-MedSpeed | Søndag 3.tidsperiode. Drift Tilstand. 0-OFF, 1-Lav Hastighed, 2-Høj Hastighed, 6-Medium Hastighed | Sunday: Third period operating mode: 0=OFF, 1=low speed, 2=high speed , 6=medium speed
0x3865 | AHU controller | Week Schedule | Standard | TimeSw-Mode21 |  | 4x0138 | x.xx | AV126 | x.xx | 0 | 6 | 1 | Mode Zone21 0-OFF, 1-LoSpeed, 2-HiSpeed, 6-MedSpeed | Mandag 4.tidsperiode. Drift Tilstand. 0-OFF, 1-Lav Hastighed, 2-Høj Hastighed, 6-Medium Hastighed | Monday: Fourth period operating mode: 0=OFF, 1=low speed, 2=high speed , 6=medium speed
0x3866 | AHU controller | Week Schedule | Standard | TimeSw-Mode22 |  | 4x0139 | x.xx | AV127 | x.xx | 0 | 6 | 1 | Mode Zone22 0-OFF, 1-LoSpeed, 2-HiSpeed, 6-MedSpeed | Tirsdag 4.tidsperiode. Drift Tilstand. 0-OFF, 1-Lav Hastighed, 2-Høj Hastighed, 6-Medium Hastighed | Tuesday: Fourth period operating mode: 0=OFF, 1=low speed, 2=high speed , 6=medium speed
0x3867 | AHU controller | Week Schedule | Standard | TimeSw-Mode23 |  | 4x0140 | x.xx | AV128 | x.xx | 0 | 6 | 0 | Mode Zone23 0-OFF, 1-LoSpeed, 2-HiSpeed, 6-MedSpeed | Onsdag 4.tidsperiode. Drift Tilstand. 0-OFF, 1-Lav Hastighed, 2-Høj Hastighed, 6-Medium Hastighed | Wednesday: Fourth period operating mode: 0=OFF, 1=low speed, 2=high speed , 6=medium speed
0x3868 | AHU controller | Week Schedule | Standard | TimeSw-Mode24 |  | 4x0141 | x.xx | AV129 | x.xx | 0 | 6 | 2 | Mode Zone24 0-OFF, 1-LoSpeed, 2-HiSpeed, 6-MedSpeed | Torsdag 4.tidsperiode. Drift Tilstand. 0-OFF, 1-Lav Hastighed, 2-Høj Hastighed, 6-Medium Hastighed | Thursday: Fourth period operating mode: 0=OFF, 1=low speed, 2=high speed , 6=medium speed
0x3869 | AHU controller | Week Schedule | Standard | TimeSw-Mode25 |  | 4x0142 | x.xx | AV130 | x.xx | 0 | 6 | 1 | Mode Zone25 0-OFF, 1-LoSpeed, 2-HiSpeed, 6-MedSpeed | Fredag 4.tidsperiode. Drift Tilstand. 0-OFF, 1-Lav Hastighed, 2-Høj Hastighed, 6-Medium Hastighed | Friday: Fourth period operating mode: 0=OFF, 1=low speed, 2=high speed , 6=medium speed
0x386A | AHU controller | Week Schedule | Standard | TimeSw-Mode26 |  | 4x0143 | x.xx | AV131 | x.xx | 0 | 6 | 1 | Mode Zone26 0-OFF, 1-LoSpeed, 2-HiSpeed, 6-MedSpeed | Lørdag 4.tidsperiode. Drift Tilstand. 0-OFF, 1-Lav Hastighed, 2-Høj Hastighed, 6-Medium Hastighed | Saturday: Fourth period operating mode: 0=OFF, 1=low speed, 2=high speed , 6=medium speed
0x386B | AHU controller | Week Schedule | Standard | TimeSw-Mode27 |  | 4x0144 | x.xx | AV132 | x.xx | 0 | 6 | 0 | Mode Zone27 0-OFF, 1-LoSpeed, 2-HiSpeed, 6-MedSpeed | Søndag 4.tidsperiode. Drift Tilstand. 0-OFF, 1-Lav Hastighed, 2-Høj Hastighed, 6-Medium Hastighed | Sunday: Fourth period operating mode: 0=OFF, 1=low speed, 2=high speed , 6=medium speed
0x3460 | AHU controller | Control | Standard | TempRegMode |  | 4x0148 | x.xx | AV133 | x.xx | 0 | 3 | 0 | 0-Sup, 1-Ext, 2-Room, 3-Sup/Ext -Diff | 0-tilluft, 1-fraluft, 2-Rum, 3-tilluft/fraluft. Diff | 0=supply, 1-Extract, 2=Room, 3=supply/extract differential
0x3461 | AHU controller | Set point | Standard | TempRegSet | °C | 4x0149 | x.xx | AV134 | x.xx | 0 | 4000 |  | TempSet for actual RegMode [1/100°C] | Temperatur setpunkt for aktuel reguleringsform [1/100°C] | Temperature setpoint for actual control type [1/100°C]
0x3101 | AHU controller | Set point | Standard | SupTempMinSet | °C | 4x0150 | x.xx | AV135 | x.xx | 0 | 4000 | 1000 | Min Allowed SupplyTemp [1/100°C] | Min. begrænsning tillufts temperatur [1/100°C] | Min. limit supply temperature [1/100°C]
0x3102 | AHU controller | Set point | Standard | SupTempMaxSet | °C | 4x0151 | x.xx | AV136 | x.xx | 2000 | 5000 | 3500 | Max Allowed SupplyTemp [1/100°C] | Max. begrænsning tillufts temperatur [1/100°C] | Max. limit supply temperature [1/100°C]
0x3103 | AHU controller | Set point | Standard | SupTempDiffSet | °C | 4x0152 | x.xx | AV137 | x.xx | 100 | 1500 | 300 | Setpoint: Temperature differential between supply and extract. Only relevant when TempRegMode is 3 (supply/extract differential) (constant supply/extract - differential temperature control) [1/100°C] | Setpunkt: Temperatur differens mellem tilluft/fraluft. KUN AKTUEL for TempRegMode = 3-tilluft/fraluft. Diff (Konst tilluft/fraluft. -Diff.TempReg) [1/100°C] | Setpoint: Temperature differential between supply and extract. Only relevant when TempRegMode is 3 (supply/extract differential) (constant supply/extract - differential temperature control) [1/100°C]
| AHU controller | Alarm | Standard | SupTempDif2Alr | °C | 4x0155 | x.xx | NA | x.xx | 200 | 1500 | 500 |  |  | Alarm limit for temperature differential between supply setpoint and actual value [1/100°C]
0x3108 | AHU controller | Alarm | Standard | SupTempDiffAlr | °C | 4x0156 | x.xx | AV138 | x.xx | 200 | 1500 | 500 | Alarm limit for temperature differential between supply setpoint and actual value [1/100°C] | Alarm Grænse for temp. diff. mellem tilluft setpunkt og aktuel værdi [1/100°C] | Alarm limit for temperature differential between supply setpoint and actual value [1/100°C]
0x3110 | Heating | Control | Standard | SupTempHeatPB | °C | 4x0157 | x.xx | AV139 | x.xx | 200 | 10000 | 750 | P-Band for Supply TempReg heating [1/100°C] | P-Bånd for tilluft temp. regulering [1/100°C] | P-band for supply air temperature control [1/100°C]
0x3111 | Cooling coil | Control | Standard | SupTempCool_IT | sec | 4x0158 | x.xx | AV140 | x.xx | 10 | 30000 | 700 | I-Time for Reg on CoolOut [sec] | I-Tid for Reg. køling tilluft[sec] | I-time for supply cooling control [sec]
0x3112 | Heat exchanger | Control | Standard | SupTempEXC_IT | sec | 4x0159 | x.xx | AV141 | x.xx | 10 | 30000 | 120 | I-Time for Reg on EXC Out [sec] | I-Tid for Reg. veksler tilluft [sec] | I-time for supply heat exchanger control [sec]
0x3113 | Heating | Control | Standard | SupTempHeat_IT | sec | 4x0160 | x.xx | AV142 | x.xx | 10 | 30000 | 300 | I-Time for Reg on Heat Out [sec] | I-Tid for Reg. Varme tilluft [sec] | I-time for supply heating control [sec]
0x3114 | Fan | Control | Standard | SupTempDnRegIt | sec | 4x0161 | x.xx | AV143 | x.xx | 10 | 30000 | 120 | I-Time for SupTempReg Flow DownReg Out [sec] | I-Tid for flow nedregulering af tilluft ved lav tilluftstemp. [sec] | I-time for supply flow reduction in case of low supply temperature [sec]
0x3105 | Heater 2 | Control | Standard | SupTempHeat2IT | sec | 4x0162 | x.xx | NA | NA | 10 | 30000 | 300 | I-Time for Reg on Heat2 Out [sec] | I-Tid for Reg. Varme2 tilluft (sec) | I-time for supply heating2 control [sec]
0x3109 | Heat pump | Control | Speciel | SupTempHP_IT | sec | 4x0164 | x.xx | NA | NA | 10 | 30000 | 300 | I-Time for supply tempReg Heat pump while heating [sec] | I-Tid for Reg Varmepumpe | I-time for heat pump[sec]
0x3208 | Heating | Alarm |  | ExtTempDiffAlr | °C | 4x0165 | x.xx | AV144 | x.xx | 200 | 1500 | 500 | TempDiff between Set/Meas Alarm Limit [1/100°C] | Alarm Grænse for temp. diff. mellem setpunkt og aktuel værdi på fraluftstemperatur [1/100°C] | Alarm limit for temperature differential between extract setpoint and actual value [1/100°C]
0x3210 | Heating | Control |  | ExtTempHeatPB | °C | 4x0166 | x.xx | AV145 | x.xx | 200 | 10000 | 500 | P-Band for Extract TempReg heating [1/100°C] | P-Bånd for fraluft temp. regulering [1/100°C] | P-band for extract air temperature control [1/100°C]
0x3211 | Cooling coil | Control | Standard | ExtTempCool_It | sec | 4x0167 | x.xx | AV146 | x.xx | 10 | 30000 | 1000 | I-Time for Reg on CoolOut [sec] | I-Tid for Reg. Køling fraluft [sec] | I-time for extract cooling control [sec]
0x3212 | Heat exchanger | Control | Standard | ExtTempEXC_It | sec | 4x0168 | x.xx | AV147 | x.xx | 10 | 30000 | 300 | I-Time for Reg on EXC Out [sec] | I-Tid for Reg. veksler fraluft [sec] | I-time for extract heat exchanger control [sec]
0x3213 | Heating | Control | Standard | ExtTempHeat_It | sec | 4x0169 | x.xx | AV148 | x.xx | 10 | 30000 | 600 | I-Time for Reg on Heat Out [sec] | I-Tid for Reg. varme fraluft [sec] | I-time for extract heating control [sec]
0x3214 | Fan | Control | Standard | ExtTempDnRegIt | sec | 4x0170 | x.xx | AV149 | x.xx | 10 | 30000 | 300 | I-Time for ExtTempReg Flow DownReg Out [sec] | I-Tid for flow nedregulering af fraluft ved lav tilluftstemp.[sec] | I-time for extract flow reduction in case of low supply temperature [sec]
0x3215 | Heater 2 | Control | Standard | ExtTempHeat2It | sec | 4x0171 | x.xx | NA | NA | 10 | 30000 | 600 | I-Time for Reg on Heat2 Out [sec] | I-Tid for Reg. Varme 2 [sec] | I-time for heating 2 control [sec]
0x3209 | Heat pump | Control | Standard | ExtTempHP_IT | sec | 4x0173 | x.xx | NA | NA | 10 | 30000 | 600 | I-Time for extract tempReg Heat pump while heating [sec] | I-Tid for Reg. Varmepumpe [sec] | I-time for heat pump control [sec]
0x3380 | AHU controller | Summer/Winter comp. | Standard | SWTC_WintX1 | °C | 4x0175 | x.xx | AV150 | x.xx | -3000 | 0 | -1500 | Sum/Wint-TempComp Winter Lo OutDoor TempSet [1/100°C] | Sommer/Vinter-Temp.Komp. vinter Lav Ude Temp.Setpunkt [1/100°C] | Summer/winter temp. comp.: low outdoor temp. setpoint, winter [1/100°C]
0x3381 | AHU controller | Summer/Winter comp. | Standard | SWTC_WintX2 | °C | 4x0176 | x.xx | AV151 | x.xx | -1000 | 1000 | 0 | Sum/Wint-TempComp Winter Hi OutDoor TempSet [1/100°C] | Sommer/Vinter-Temp.Komp. vinter Høj Ude Temp.Setpunkt [1/100°C] | Summer/winter temp. comp.: high outdoor temp. setpoint, winter [1/100°C]
0x3382 | AHU controller | Summer/Winter comp. | Standard | SWTC_SumX1 | °C | 4x0177 | x.xx | AV152 | x.xx | 1000 | 3000 | 2000 | Sum/Wint-TempComp Summer Lo OutDoor TempSet [1/100°C] | Sommer/Vinter-Temp.Komp. sommer Lav Ude TempSet [1/100°C] | Summer/winter temp. comp.: low outdoor temp. setpoint, summer [1/100°C]
0x3383 | AHU controller | Summer/Winter comp. | Standard | SWTC_SumX2 | °C | 4x0178 | x.xx | AV153 | x.xx | 2000 | 4000 | 3000 | Sum/Wint-TempComp Summer Hi OutDoor TempSet [1/100°C] | Sommer/Vinter-Temp.Komp. sommer Høj UdeTempSet [1/100°C] | Summer/winter temp. comp.: high outdoor temp. setpoint, summer [1/100°C]
0x3384 | AHU controller | Summer/Winter comp. | Standard | SWTCWinComVal | °C | 4x0179 | x.xx | AV154 | x.xx | 0 | 1000 | 500 | Sum/Wint-TempComp Winter compensation [1/100°C] | Sommer/Vinter-Temp.Komp. vinter kompensation [1/100°C] | Summer/winter temp. comp.: winter compensation [1/100°C]
0x3385 | AHU controller | Summer/Winter comp. | Standard | SWTCSumComVal | °C | 4x0180 | x.xx | AV155 | x.xx | -1000 | 1000 | -500 | Sum/Wint-TempComp Summer compensation [1/100°C] | Sommer/Vinter-Temp.Komp sommer kompensation [1/100°C] | Summer/winter temp. comp.: summer compensation [1/100°C]
| Cooling coil | Alarm | Standard | C_LoPress1Alr | Bar | 4x0181 | 6.41 | AV315 | 6.41 | 0 | 10000 | 300 |  |  | LoPressSens-1 AlarmLimit [1/100 Bar]
| Cooling coil | Alarm | Standard | C_HiPress1Alr | Bar | 4x0182 | 6.41 | AV316 | 6.41 | 0 | 10000 | 1500 |  |  | HiPressSens-1 AlarmLimit [1/100 Bar]
| Cooling coil | Alarm | Standard | C_LoPress2Alr | Bar | 4x0183 | 6.41 | AV317 | 6.41 | 0 | 10000 | 300 |  |  | LoPressSens-2 AlarmLimit [1/100 Bar]
| Cooling coil | Alarm | Standard | C_HiPress2Alr | Bar | 4x0184 | 6.41 | AV318 | 6.41 | 0 | 10000 | 1500 |  |  | HiPressSens-2 AlarmLimit [1/100 Bar]
0x33D0 | AHU controller | Summer/Winter comp. | Standard | SW_Mode |  | 4x0185 | x.xx | AV156 | x.xx | 0 | 4 | 0 | Summer/Winter Mode: 0 - OFF 1 - Shift on outdoor temp 2 - Shift on date 3 - Manuel Summer 4 - Manuel Winter | Valg af Sommer/Vinter skift 0 - OFF (Ingen Sommer/Vinter-skift) 1 - Skift i henhold til udetemperatur 2 - Sommer/Vinter-skift i henhold til dato 3 - Manuel Sommer 4 - Manuel Vinter | Summer/winter changeover: 0=OFF (no summer/winter changeover) 1=Changeover determined by outdoor temperature 2=Changeover determined by date 3=Manual summer 4=Manual winter
0x33D1 | AHU controller | Summer/Winter comp. | Standard | SW_OutWinterON | °C | 4x0186 | x.xx | AV157 | x.xx | -3000 | 4000 | 0 | OutdoorTemp for start WinterMode (SW_Mode = 1) | Ude Temp. for start vinter drift (SW_Mode = 1) [1/100°C] | Outdoor temperature for start of winter operation (SW_Mode = 1) [1/100°C]
0x33D2 | AHU controller | Summer/Winter comp. | Standard | SW_OutSummerON | °C | 4x0187 | x.xx | AV158 | x.xx | -3000 | 4000 | 2000 | OutdoorTemp for start SummerMode (SW_Mode = 1) | Ude Temp. for start sommer drift (SW_Mode = 1) [1/100°C] | Outdoor temperature for start of summer operation (SW_Mode = 1) [1/100°C]
0x33D3 | AHU controller | Summer/Winter comp. | Standard | SW_MonthWintON |  | 4x0188 | x.xx | AV159 | x.xx | 7 | 12 | 11 | Month for Start WinterMode (SW_Mode = 2) | Måned for start vinter drift (SW_Mode = 2) | Month for start of winter operation (SW_Mode = 2)
0x33D4 | AHU controller | Summer/Winter comp. | Standard | SW_DateWintON |  | 4x0189 | x.xx | AV160 | x.xx | 1 | 31 | 1 | Date for Start WinterMode (SW_Mode = 2) | Dato for start vinter drift (SW_Mode = 2) | Date for start of winter operation (SW_Mode = 2)
0x33D5 | AHU controller | Summer/Winter comp. | Standard | SW_MonthSumON |  | 4x0190 | x.xx | AV161 | x.xx | 1 | 6 | 5 | Month for Start SummerMode (SW_Mode = 2) | Måned for start sommer drift (SW_Mode = 2) | Month for start of summer operation (SW_Mode = 2)
0x33D6 | AHU controller | Summer/Winter comp. | Standard | SW_DateSumON |  | 4x0191 | x.xx | AV162 | x.xx | 1 | 31 | 1 | Date for Start SummerMode (SW_Mode = 2) | Dato for start sommer drift (SW_Mode = 2) | Date for start of summer operation (SW_Mode = 2)
0x33E0 | Damper, Recirculation | Set point | Standard | RecicStartTmp | °C | 4x0195 | x.xx | AV163 | x.xx | 500 | 4000 | 1900 | StartTemp for Recirc Function [1/100 °C] | Start Temp. for Recirk. funktion [1/100 °C] | Startup temperature for recirculation [1/100 °C]
0x33E1 | Damper, Recirculation | Set point | Standard | RecicStopTmp | °C | 4x0196 | x.xx | AV164 | x.xx | 500 | 4000 | 2100 | StopTemp for Recirc Function [1/100 °C] | Stop Temp. for Recirk. funktion [1/100 °C] | Stop temperature for recirculation [1/100 °C]
| Damper, Recirculation | Set point | Special | RecicStartTmp2 |  | 4x0197 | x.xx | AV295 | x.xx | 500 | 4000 | 2100 | StopTemp for Recirc Function [1/100 °C] | Stop Temp. for Recirk. funktion [1/100 °C] | Start temperature for recirculation [1/100 °C]
| Damper, Recirculation | Set point | Special | RecicStopTmp2 |  | 4x0198 | x.xx | AV296 | x.xx | 500 | 4000 | 2100 | StopTemp for Recirc Function [1/100 °C] | Stop Temp. for Recirk. funktion [1/100 °C] | Stop temperature for recirculation [1/100 °C]
| Damper, Recirculation | Set point | Special | RecSwitchTmp2 |  | 4x0199 | x.xx | AV297 | x.xx | 500 | 4000 | 2100 | StopTemp for Recirc Function [1/100 °C] | Stop Temp. for Recirk. funktion [1/100 °C] | Switch temperature for recirculation [1/100 °C]
0x3104 | AHU controller | Fire |  | SupTempFireAlr | °C | 4x0200 | x.xx | AV165 | x.xx | 5000 | 12000 | 8000 | SupplyTempSet for Internal FireAlr [1/100°C] | Setpunkt for intern brand Alarm i tilluft [1/100°C] | Setpoint for internal fire alarm in supply duct [1/100°C]
0x3204 | AHU controller | Fire |  | ExtTempFireAlr | °C | 4x0201 | x.xx | AV166 | x.xx | 3500 | 12000 | 7000 | ExtractTempSet for Internal FireAlr [1/100°C] | Setpunkt for intern brand Alarm i fraluft. [1/100°C] | Setpoint for internal fire alarm in extract duct [1/100°C]
0x3420 | Cooling coil | Control | Standard | CoolFlwForcePc | % | 4x0205 | x.xx | AV167 | x.xx | 0 | 10000 | 2500 | Cool-FlowForce Percent Set [1/100 %] | Forøgelse af hastighed når køling er aktiv [Pct] | Increase in fan speed when cooling is active [%]
0x3421 | Cooling coil | Set point | Standard | CoolOutTmpMin | °C | 4x0206 | x.xx | AV168 | x.xx | 0 | 3000 | 1500 | Min OutDoorTemp for CoolAgg. Active | Min. Udetemperatur for start af køleanlæg | Min. outdoor temperature for start of cooling
0x3422 | Cooling coil | Set point | Standard | CoolSupMinTmp | °C | 4x0207 | x.xx | AV169 | x.xx | 0 | 2500 | 1200 | Min SupplyTemp for Cool (Used for RoomReg) | Min. tilluft temp. når Køling er aktiv (KUN for Rumregulering) | Min. supply temperature when cooling is active (only with room temp. control)
0x3370 | AHU controller | Summer Night Cooling | Standard | SN_ExtTmpStart | °C | 4x0210 | x.xx | AV170 | x.xx | 1500 | 4000 | 2300 | SummerNight Ext/Room Temp Start [1/100°C] | Sommer Nat fraluft./Rum Temp. Start [1/100°C] | Summer night extract/room temp. start [1/100°C]
0x3371 | AHU controller | Summer Night Cooling | Standard | SN_ExtTmpStop | °C | 4x0211 | x.xx | AV171 | x.xx | 1000 | 3000 | 2000 | SummerNight Ext/Room Temp Stop [1/100°C] | Sommer Nat fraluft./Rum Temp. Stop [1/100°C] | Summer night extract/room temp. stop [1/100°C]
0x3372 | AHU controller | Summer Night Cooling | Standard | SN_OutTmpStart | °C | 4x0212 | x.xx | AV172 | x.xx | 500 | 2000 | 1200 | SummerNight OutDoor Temp Start [1/100°C] | Sommer Nat Ude Temp. Start [1/100°C] | Summer night outdoor temp. start [1/100°C]
0x3373 | AHU controller | Summer Night Cooling | Standard | SN_SupTmpSet | °C | 4x0213 | x.xx | AV173 | x.xx | 500 | 2000 | 1000 | SummerNight SupTemp Reg Set [1/100°C] | Sommer Nat tilluft Temp. Reg. Set [1/100°C] | Summer night supply temp. control setpoint [1/100°C]
0x3374 | AHU controller | Summer Night Cooling | Standard | SN_StartTime | Min | 4x0214 | x.xx | AV174 | x.xx | 0 | 1439 | 1380 | SummerNight StartTime [Min] 20:00 - 02-00, in server checked! | Sommer Nat Start [Min] | Summer night start [min]
0x3375 | AHU controller | Summer Night Cooling | Standard | SN_StopTime | Min | 4x0215 | x.xx | AV175 | x.xx | 0 | 1439 | 360 | SummerNight StopTime [Min] 03:00 - 08:00, in server checked! | Sommer Nat Stop [Min] | Summer night stop [min]
0x3320 | Heat exchanger | Set point | Special | CExcDeIceTemp | °C | 4x0220 | x.xx | AV176 | x.xx | -500 | 2000 | 500 | Min ExhaustTempSet for Cross EXC [1/100°C] | Min. afkast temp. setpunkt på kryds varmeveksler [1/100°C] | Min. exhaust temp setpoint for cross-flow heat exchanger [1/100°C]
0x3321 | Heat exchanger | Control | Special | CExcDeIceTempP | °C | 4x0221 | x.xx | AV177 | x.xx | 200 | 2000 | 500 | P-Band for BypaasReg for Cross EXC [1/100°C] | P-Bånd for By-pass Regulator på kryds varmeveksler [1/100°C] | P-band for bypass control of cross-flow heat exchanger [1/100°C]
0x3323 | Heat exchanger | Set point | Special | CExcDeIcePress | Pa | 4x0222 | x.xx | AV313 | 6.41 | 10 | 5000 | 30 | Pressure to start deicing of cross Exc. [Pa] | Setpunkt trykfald over krydsveksler for start afisning [Pa] | Setpoint for pressure drop across cross-flow exchanger for start of de-icing [Pa]
0x3324 | Heat exchanger | Control | Special | CExcDeIceTime | Sec | 4x0223 | x.xx | AV314 | 6.41 | 180 | 1800 | 300 | Time for deicing cross exc. when pressure monitored. | Setpunkt tid for afisning af krydsveksler [sec] | Setpoint for duration of heat exchanger de-icing [sec]
0x3920 | Heat exchanger | Control | Standard | BattEXC_PumpFc |  | 4x0225 | x.xx | AV178 | x.xx | 0 | 3 | 1 | WaterCoil EXC PumpFunc: 0 -> Pump always ON 1 -> Pump ON when EXC HeatPower > 0 (AutoMode) 2 -> Pump ON when OutDoorTemp < PumpStartTemp 3 -> Pump ON when ExcPower > PmpStartPrc | Funktion af cirk. Pumpe på væskekoblet flade: 0 -> Pumpe kører konstant 1 -> Pumpe kører når genvindingsbehov > Indstillet værdi adresse 268 (CoilEXCPmpStPr) 2 -> Pumpe kører når UdeTemp. < Pumpe Start Temp. Setpunkt | Circulation pump mode on heat exchanger coil: 0 –> Pump runs constantly 1 –> Pump runs if heat recovery demand is > 0 (AutoMode) 2 –> Pump runs if outdoor temp. is < temp. setpoint for pump start
0x3921 | Heat exchanger | Control | Standard | BattEXC_PumpSt | °C | 4x0226 | x.xx | AV179 | x.xx | 0 | 4000 | 1500 | Startup temp. setpoint for circulation pump on heat exchanger coil ONLY used if CoilEXC_PumpFunc (Address 224) = 2. Pump runs if outdoor temp. is < temp. setpoint for pump start | Start Setpunkt for Cirk.Pumpe på væskekoblet flade Bruges KUN sammen med CoilEXC_PumpFunc (Address 224) = 2. Pumpe kører når Udetemperatur < Temp. Setpunkt Pumpe Start | Startup temp. setpoint for circulation pump on heat exchanger coil ONLY used if CoilEXC_PumpFunc (Address 224) = 2. Pump runs if outdoor temp. is < temp. setpoint for pump start
0x3922 | Heat exchanger | Alarm | Standard | BattEXC_AlrSet | °C | 4x0227 | x.xx | AV180 | x.xx | -1000 | 2000 | 800 | Temp. differential alarm setpoint for heat exchanger coil Alarm activated if temperature differential (in relation to outdoor temp.) downstream from heat exchanger coil operating at 50% power (or more) is lower than the alarm setpoint | Temp.Diff. Alarm Setpunkt på Varmevekslerflade Alarm når Temp.Diff. (i forhold til UdeTemp.) efter Varmeveksler-flade ved 50% effekt (eller mere) er lavere end Alarm Setpunkt, | Temp. differential alarm setpoint for heat exchanger coil Alarm activated if temperature differential (in relation to outdoor temp.) downstream from heat exchanger coil operating at 50% power (or more) is lower than the alarm setpoint
0x3478 | Humidity | Set point | Standard | Humid_SupSet | % | 4x0228 | x.xx | AV304 | 6.12 | 0 | 10000 | 2000 | Huminifier Supply Setpoint [1/100%] RH | Fugtsetpunkt for valgt reguleringsform (tilluft/fraluftn.) [1/100%] RH | Humidity setpoint for selected control type (supply/exhaust) [1/100%] RH
0x3330 | Heating coil 1, Water | Set point | Standard | HW1UpStartPow | % | 4x0230 | x.xx | AV181 | x.xx | 0 | 10000 | 5000 | HeatWaterCoil Upstart PowerSet [1/100%] | Varmeflade 1: Opstart Effekt Setpunkt [1/100%] | Heating coil: Startup power setpoint [1/100%]
0x3331 | Heating coil 1, Water | Control | Standard | HW1PumpFunc |  | 4x0231 | x.xx | AV182 | x.xx | 0 | 3 | 1 | HeatWaterCoil PumpFunc: 0 -> Pump always ON 1 -> Pump ON when HeatPower > 0 (AutoMode) 2 -> Pump ON when OutDoorTemp < PumpStartTemp 3 -> Pump ON when HeatPower > PmpStartPrc | Varmeflade 1 Funktion af cirkulationspumpe: 0 -> Pumpe kører konstant 1 -> Pumpe kører når %-åbning på varmeventil > Indstillet værdi i adresse = 236 2 -> Pumpe kører når Udetemperatur > Pumpe Start Temp. Setpunkt (Adresse = 231) | Circulation pump mode on heating coil: 0 –> Pump runs constantly 1 –> Pump runs if heat demand is > 0 (AutoMode) 2 –> Pump runs if outdoor temp. is < temp. setpoint for pump start
0x3332 | Heating coil 1, Water | Set point | Standard | HW1PmpStartTmp | °C | 4x0232 | x.xx | AV183 | x.xx | 500 | 3000 | 1500 | HeatWaterCoil PumpStartTemp. Is used together with WaterPumpFunc = 2. Pump = ON when OutDoorTemp < PumpStartTemp | Varmeflade 1 Starttemperatur for Cirk.pumpe på varmeflade 1 Bruges KUN sammen med WaterPumpFunc (Address 230) = 2 Pumpe kører når Udetemperatur < Temp. Setpunkt Pumpe Start | Startup temp. setpoint for circulation pump on heating coil ONLY used if HW_PumpFunc (Address 230) = 2 Pump runs if outdoor temp. is < temp. setpoint for pump start
0x3333 | Heating coil 1, Water | Set point | Standard | HW1FrzStopSet | °C | 4x0233 | x.xx | AV184 | x.xx | 500 | 4000 | 2500 | SetVal for AntiFrost Reg when Agg. = Stop [1/100°C] | Varmeflade 1 - Setpunkt for Anti-Frost Reg når anlægget = Stop [1/100°C] | Setpoint for frost protection control when unit is in STOP mode [1/100°C]
0x3334 | Heating coil 1, Water | Set point | Standard | HW1FrzDriftSet | °C | 4x0234 | x.xx | AV185 | x.xx | 200 | 2000 | 500 | SetVal for AntiFrost Reg when Agg. = Drift [1/100°C] | Varmeflade 1 - Setpunkt for Anti-Frost Reg når anlægget = Drift [1/100°C] | Setpoint for frost prot. control when unit is in OPERATING mode [1/100°C]
0x3335 | Heating coil 1, Water | Control | Standard | HW1FreezePB | °C | 4x0235 | x.xx | AV186 | x.xx | 200 | 2000 | 500 | P-Band for AntiFrost Reg [1/100°C] | Varmeflade 1 - P-Bånd for Anti-Frost Reg [1/100°C] | P-band for frost protection control [1/100°C]
0x3336 | Heating coil 1, Water | Set point | Standard | HW1FrzAlrTpSet | °C | 4x0236 | x.xx | AV187 | x.xx | 200 | 2000 | 200 | SetVal for AntiFrost TempAlarm [1/100°C] | Varmeflade 1 - Setpunkt for Anti-Frost Temp. Alarm [1/100°C] | Setpoint for frost protection temp. alarm [1/100°C]
0x333C | Heating coil 1, Water | Set point | Standard | HW1PmpStartPrc | % | 4x0237 | x.xx | AV312 | 6.41 | 0 | 10000 | 300 | When PumpFunc=3 then pump only starts when heatingpower exceeds this setting.only Novema | Varmeflade 1 Start cirkulationspumpe ved %-åben ventil [1/100%] Bruges KUN sammen med HW1_PumpFunc (Address 230) = 1 Pumpen starter når værdien overskrides. | Heating coil 1 Start circulation pump with %-open valve [1/100%] ONLY used if HW1_PumpFunc (Address 230) = 1 The pump starts when the value is exceeded.
0x3350 | Cooling coil | Control | Standard | CW_PumpFunc |  | 4x0240 | x.xx | AV188 | x.xx | 0 | 3 | 0 | CoolWater PumpFunc: 0 -> Pump always ON 1 -> Pump ON when HeatPower > 0 (AutoMode) 2 -> Pump ON when OutDoorTemp < PumpStartTemp 3 -> Pump ON when HeatPower > PmpStartPrc | Funktion af kølevands pumpe: 0 -> Pumpe kører konstant 1 -> Pumpe kører når Køleeffekt > 0% (AutoMode) 2 -> Pumpe kører når Udetemperatur > Pumpe Start Temp. Setpunkt | Cooling water pump mode: 0 –> Pump runs constantly 1 –> Pump runs if cooling power is > 0 (AutoMode) 2 –> Pump runs if outdoor temp. > temp. setpoint for pump start
0x3351 | Cooling coil | Set point | Standard | CW_PmpStartTmp | °C | 4x0241 | x.xx | AV189 | x.xx | 500 | 4000 | 2100 | Temp. setpoint for start of cooling coil pump ONLY used if CW_PumpFunc (Address 239) = 2 Pump runs if outdoor temp. is > temp. setpoint for pump start | Temp. setpunkt for start af køleflade pumpe Bruges KUN sammen med WaterPumpFunc (Address 239) = 2 Pumpe kører når UdeTemp. > Pumpe start temp. setpunkt | Temp. setpoint for start of cooling coil pump ONLY used if CW_PumpFunc (Address 239) = 2 Pump runs if outdoor temp. is > temp. setpoint for pump start
0x3475 | GreenZone | Set point | Standard | FanOptSupExtIn | % | 4x0242 | x.xx | AV223 | x.xx | 0 | 10000 |  | Extern Signal Greenzone, Supply | Extern Signal Greenzone, tilluft [1/100%] | External signal GreenZone, supply [1/100%]
0x3476 | GreenZone | Set point | Standard | FanOptExtExtIn | % | 4x0243 | x.xx | AV224 | x.xx | 0 | 10000 |  | Extern Signal Greenzone, Extract | Extern Signal Greenzone, fraluft [1/100%] | External signal GreenZone, exhaust [1/100%]
0x3390 | Filter | Alarm | Standard | FiltSupStatAlr | Pa | 4x0245 | x.xx | AV190 | x.xx | 10 | 500 | 80 | Filter Pressure Alr Limit for SupFilter (static mode) | Alarm grænse for trykfald tilluft filter (static mode) | Alarm limit for pressure drop across intake filter (static mode)
0x3391 | Filter | Alarm | Standard | FiltExtStatAlr | Pa | 4x0246 | x.xx | AV191 | x.xx | 10 | 500 | 80 | Filter Pressure Alr Limit for ExtFilter (static mode) | Alarm grænse for trykfald fraluft filter (static mode) | Alarm limit for pressure drop across exhaust filter (static mode)
0x3392 | Filter | Alarm | Standard | FiltSupDynAlr | % | 4x0247 | x.xx | AV192 | x.xx | 1000 | 10000 | 5000 | Filter Pressure Alr Limit for SupFilter (dynamic mode) | Alarm grænse for trykfald tilluft filter (dynamic mode) | Alarm limit for pressure drop across intake filter (dynamic mode)
0x3393 | Filter | Alarm | Standard | FiltExtDynAlr | % | 4x0248 | x.xx | AV193 | x.xx | 1000 | 10000 | 5000 | Filter Pressure Alr Limit for ExtFilter (dynamic mode) | Alarm grænse for trykfald fraluft filter (dynamic mode) | Alarm limit for pressure drop across exhaust filter (dynamic mode)
0x339B | Filter | Alarm | Standard | FiltSup2StaAlr | Pa | 4x0249 | 4.18 | AV258 | 4.18 | 10 | 500 | 80 | Filter Pressure Alr Limit for SupFilter2 (static mode) | Tilluft Filter2 Filtertryk Alarmgrænse for (statisk) | Filter Pressure Alr Limit for SupFilter2 (static mode)
0x3E07 | AHU controller | Alarm | Standard | Alr_MailSetup |  | 4x0250 | x.xx | AV194 | x.xx | 0 | 3 | 3 | Alarm Mail Config: 0 - Mail are not send 1 - Mail on A-Alarm 2 - Mail on B-Alarm 3 - Mail on A and B Alarm | Alarm Mail Opsætning 0 - Mail er ikke sendt 1 - Mail er sendt på A-Alarm 2 - Mail er sendt på B-Alarm 3 - Mail er sendt på A og B Alarm | Alarm email setup 0 –> Emails not sent 1 –> Emails sent for A-alarms 2 –> Emails sent for B-alarms 3 –> Emails sent for A and B-alarms
0x3005 | AHU controller | Alarm | Standard | UserRE_Func |  | 4x0251 | x.xx | AV195 | x.xx | 0 | 4 | 0 | User RE (B-Alarm relay) Function: 0 –> B-alarm 1 –> Low speed indication 2 –> High speed indication 3 -> Medium speed indication | Funktion på B-alarmrelæ: 0 - B-Alarm 1 - Lav Hastighed indikator 2 - Høj Hastighed indikator 3 - Medium Hastighed indikator | User RE (B-Alarm relay) Function: 0 –> B-alarm 1 –> Low speed indication 2 –> High speed indication 3 -> Medium speed indication
0x34C5 | Preheater coil | Set point | Standard | PHStartPrc | % | 4x0252 | x.xx | AV206 | x.xx | 0 | 30000 | 5000 | Pre-heating coil - Start-up output setpoint [1/100%]; when system is in start-up sequence | Forvarmeflade - Opstart Effekt Setpunkt [1/100%]; når anlægget er i opstartssekvens | Pre-heating coil - Start-up output setpoint [1/100%]; when system is in start-up sequence
0x34CC | Preheater coil | Control | Standard | PHPumpMode |  | 4x0253 | x.xx | AV210 | x.xx | 0 | 4 | 0 | Pre-heating coil Circulation pump function: 0 –> Pump runs constantly 1 –> Pump runs if heat output is > 0 (AutoMode) 2 –> Pump runs if outdoor temp. is > temp. setpoint for pump start | Forvarmeflade Funktion af cirkulationspumpe: 0 -> Pumpe kører konstant 1 -> Pumpe kører når varmeeffekt > 0% (AutoMode) 2 -> Pumpe kører når Udetemperatur > Pumpe Start Temp. Setpunkt | Pre-heating coil Circulation pump function: 0 –> Pump runs constantly 1 –> Pump runs if heat output is > 0 (AutoMode) 2 –> Pump runs if outdoor temp. is > temp. setpoint for pump start
0x34CB | Preheater coil | Set point | Standard | PHPmpStTmpH | °C | 4x0254 | x.xx | AV208 | x.xx | 500 | 3000 | 1000 | Pre-heating coil Start temperature for circulation pump of pre-heating coil. ONLY used if PHPumpMode (Address 252) = 2 Pump runs if outdoor temp. is < temp. setpoint for pump start | Forvarmeflade Starttemperatur for Cirk.pumpe på forvarmeflade Bruges KUN sammen med PHPumpMode (Address 252) = 2 Pumpe kører når Udetemperatur < Temp. Setpunkt Pumpe Start | Pre-heating coil Start temperature for circulation pump of pre-heating coil. ONLY used if PHPumpMode (Address 252) = 2 Pump runs if outdoor temp. is < temp. setpoint for pump start
0x34C4 | Preheater coil | Set point | Standard | PHStandbyTmp | °C | 4x0255 | x.xx | AV205 | x.xx | 500 | 4000 | 2500 | Pre-heating coil Setpoint for frost protection control when system is in STOP mode [1/100°C] | Forvarmeflade Setpunkt for Anti-Frost Reg når anlægget = Stop [1/100°C] | Pre-heating coil Setpoint for frost protection control when system is in STOP mode [1/100°C]
0x34CE | Preheater coil | Set point | Standard | PHFrzDrSetH | °C | 4x0256 | x.xx | AV209 | x.xx | 200 | 2000 | 500 | Pre-heating coil Setpoint for frost protection control when system is in OPERATING mode [1/100°C] | Forvarmeflade Setpunkt for Anti-Frost Reg når anlægget = Drift [1/100°C] | Pre-heating coil Setpoint for frost protection control when system is in OPERATING mode [1/100°C]
0x34C8 | Preheater coil | Control | Standard | PHeatFrzPB | °C | 4x0257 | x.xx | AV207 | x.xx | 200 | 2000 | 500 | Pre-heating coil P-band for frost protection control [1/100°C] | Forvarmeflade P-Bånd for Anti-Frost Reg [1/100°C] | Pre-heating coil P-band for frost protection control [1/100°C]
0x34C3 | Preheater coil | Alarm | Standard | PHMinAlrFrz | °C | 4x0258 | x.xx | AV204 | x.xx | -4000 | 10000 | 200 | Pre-heating coil - Frost alarm Setpoint for frost protection temperature alarm [1/100°C] | Forvarmeflade - Frostalarm Setpunkt for Anti-Frost Temp. Alarm [1/100°C] | Pre-heating coil - Frost alarm Setpoint for frost protection temperature alarm [1/100°C]
0x34C2 | Preheater coil | Set point | Standard | PHeatSet | °C | 4x0259 | x.xx | AV203 | x.xx | -3000 | 2000 | 200 | Pre-heating coil - Setpoint supply duct; just after pre-heating coil | Forvarmeflade - Setpunkt tilluftskanal; efter forvarmeflade | Pre-heating coil - Setpoint supply duct; just after pre-heating coil
0x3400 | Heating coil 2, Water | Set point | Standard | HW2UpStartPow | % | 4x0260 | x.xx | AV196 | x.xx | 0 | 10000 | 5000 | Heating coil 2 - Start-up output setpoint [1/100%] | Varmeflade 2 - Opstart Effekt Setpunkt [1/100%] | Heating coil 2 - Start-up output setpoint [1/100%]
0x3401 | Heating coil 2, Water | Control | Standard | HW2PumpFunc |  | 4x0261 | x.xx | AV197 | x.xx | 0 | 3 | 1 | Heating coil 2 Circulation pump function: 0 –> Pump runs constantly 1 -> Pump runs if heating valve %-open is > value set in address = 262 2 –> Pump runs if outdoor temp. is > temp. setpoint for pump start (address = 261) | Varmeflade 2 Funktion af cirkulationspumpe: 0 -> Pumpe kører konstant 1 -> Pumpe kører når %-åbning på varmeventil > Indstillet værdi i adresse = 262 2 -> Pumpe kører når Udetemperatur > Pumpe Start Temp. Setpunkt (Adresse = 261) | Heating coil 2 Circulation pump function: 0 –> Pump runs constantly 1 -> Pump runs if heating valve %-open is > value set in address = 262 2 –> Pump runs if outdoor temp. is > temp. setpoint for pump start (address = 261)
0x3402 | Heating coil 2, Water | Set point | Standard | HW2PmpStartTmp | °C | 4x0262 | x.xx | AV198 | x.xx | 500 | 3000 | 1500 | HeatWaterCoil PumpFunc: 0 -> Pump always ON 1 -> Pump ON when HeatPower > 0 (AutoMode) 2 -> Pump ON when OutDoorTemp < PumpStartTemp 3 -> Pump ON when HeatPower > PmpStartPrc | Varmeflade 2 Starttemperatur for Cirk.pumpe på varmeflade 2 Bruges KUN sammen med WaterPumpFunc (Address 260) = 2 Pumpe kører når Udetemperatur < Temp. Setpunkt Pumpe Start | Heating coil 2 Start temperature for circulation pump of heating coil 2 ONLY used if WaterPumpFunc (Address 260) = 2 Pump runs if outdoor temp. is < temp. setpoint for pump start
0x340C | Heating coil 2, Water | Set point | Standard | HW2PmpStartPrc | % | 4x0263 | x.xx | AV311 | 6.41 | 0 | 10000 | 300 | Heating coil 2 - Start circulation pump with %-open valve. ONLY used if HW2_PumpFunc (Address 260) = 1 The pump starts when the value is exceeded. | Varmeflade 2 - Start cirkulationspumpe ved %-åben ventil. Bruges KUN sammen med HW2_PumpFunc (Address 260) = 1 Pumpen starter når værdien overskrides. | Heating coil 2 - Start circulation pump with %-open valve. ONLY used if HW2_PumpFunc (Address 260) = 1 The pump starts when the value is exceeded.
0x3403 | Heating coil 2, Water | Set point | Standard | HW2FrzStopSet | °C | 4x0264 | x.xx | AV199 | x.xx | 500 | 4000 | 2500 | Heating coil 2 - Setpoint for frost protection control when unit is in STOP mode [1/100°C] | Varmeflade 2 - Setpunkt for Anti-Frost Reg når anlægget = Stop [1/100°C] | Heating coil 2 - Setpoint for frost protection control when unit is in STOP mode [1/100°C]
0x3404 | Heating coil 2, Water | Set point | Standard | HW2FrzDriftSet | °C | 4x0265 | x.xx | AV200 | x.xx | 200 | 2000 | 500 | Heating coil 2 - Setpoint for frost protection control when unit is in OPERATING mode [1/100°C] | Varmeflade 2 - Setpunkt for Anti-Frost Reg når anlægget = Drift [1/100°C] | Heating coil 2 - Setpoint for frost protection control when unit is in OPERATING mode [1/100°C]
0x3405 | Heating coil 2, Water | Control | Standard | HW2FreezePB | °C | 4x0266 | x.xx | AV201 | x.xx | 200 | 2000 | 500 | Heating coil 2 - P-band for frost protection control [1/100°C] | Varmeflade 2 - P-Bånd for Anti-Frost Reg [1/100°C] | Heating coil 2 - P-band for frost protection control [1/100°C]
0x3406 | Heating coil 2, Water | Alarm | Standard | HW2FrzAlrTpSet | °C | 4x0267 | x.xx | AV202 | x.xx | 200 | 2000 | 200 | Heating coil 2 - Setpoint for frost protection temperature alarm [1/100°C] | Varmeflade 2 - Setpunkt for Anti-Frost Temp. Alarm [1/100°C] | Heating coil 2 - Setpoint for frost protection temperature alarm [1/100°C]
0x3352 | Cooling coil | Set point | Standard | CW_PumpStartPr | % | 4x0268 | x.xx | AV310 | 6.41 | 0 | 10000 | 2500 | Cooling coil (hydronic cooling) - Start circulation pump with %-open valve ONLY used if CW_PumpFunc (Address 239) = 1. The pump starts when the value is exceeded. | Køleflade (Vandkøling) - Start cirkulationspumpe ved %-åben ventil. Bruges KUN sammen med CW_PumpFunc (Address 239) = 1 Pumpen starter når værdien overskrides. | Cooling coil (hydronic cooling) - Start circulation pump with %-open valve ONLY used if CW_PumpFunc (Address 239) = 1. The pump starts when the value is exceeded.
0x3923 | Heat exchanger | Set point | Standard | BattEXCPmpStPr | % | 4x0269 | x.xx | AV309 | 6.41 | 0 | 10000 | 2500 | Heat exchange coil - Start circulation pump with %-open valve. ONLY used if CoilEXC_PumpFc (Address 224) = 1. The pump starts when the value is exceeded. | Varmeveksler flade - Start cirkulationspumpe ved %-åben ventil. Bruges KUN sammen med CoilEXC_PumpFc (Address 224) = 1 Pumpen starter når værdien overskrides. | Heat exchange coil - Start circulation pump with %-open valve. ONLY used if CoilEXC_PumpFc (Address 224) = 1. The pump starts when the value is exceeded.
0x3358 | Heat pump | Set point | Special | HP_MinOpTemp1 | °C | 4x0270 | x.xx | AV215 | x.xx | -4000 | 4000 | 1000 | Min air temp at outdoor coil for the heat pump to operate Relay 1 | Min. udetemperatur for aktivering varmepumpe relæ no. 1 | Min. outdoor temperature for activating heat pump relay no. 1
0x3359 | Heat pump | Set point | Special | HP_MinOpTemp2 | °C | 4x0271 | x.xx | AV216 | x.xx | -4000 | 4000 | 1000 | Min air temp at outdoor coil for the heat pump to operate Relay 2 | Min. udetemperatur for aktivering varmepumpe relæ no. 2 | Min. outdoor temperature for activating heat pump relay no. 2
0x335A | Heat pump | Set point | Special | HP_MinOpTemp3 | °C | 4x0272 | x.xx | AV217 | x.xx | -4000 | 4000 | 1000 | Min air temp at outdoor coil for the heat pump to operate Relay 3 | Min. udetemperatur for aktivering varmepumpe relæ no. 3 | Min. outdoor temperature for activating heat pump relay no. 3
0x335B | Heat pump | Set point | Special | HP_MinOpTemp4 | °C | 4x0273 | x.xx | AV218 | x.xx | -4000 | 4000 | 1000 | Min air temp at outdoor coil for the heat pump to operate Relay 4 | Min. udetemperatur for aktivering varmepumpe relæ no. 4 | Min. outdoor temperature for activating heat pump relay no. 4
0x3410 | Combi coil | Set point | Standard | CombiUpStPow | % | 4x0275 | x.xx | AV286 | 4.22 | 0 | 10000 | 5000 | CombiHeatWaterCoil Upstart PowerSet [1/100%] | Kombiflade - Opstart Effekt Setpunkt [1/100%] | Combi coil - Start-up output setpoint [1/100%]
0x3411 | Combi coil | Control | Standard | CombiPumpFunc |  | 4x0276 | x.xx | AV287 | 4.22 | 0 | 3 | 1 | Combi coil Circulation pump function: 0 –> Pump runs constantly 1 -> Pump runs if valve %-open is > value set in address = 277 2 –> Pump runs if outdoor temp. is > temp. setpoint for pump start (address = 276) | Kombiflade Funktion af cirkulationspumpe: 0 -> Pumpe kører konstant 1 -> Pumpe kører når %-åbning på ventil > Indstillet værdi (reg 4x0278) 2 -> Pumpe kører når Udetemperatur > Pumpe Start Temp. Setpunkt (reg 4x0277) | Combi coil Circulation pump function: 0 –> Pump runs constantly 1 -> Pump runs if valve %-open is > value set in address = 277 2 –> Pump runs if outdoor temp. is > temp. setpoint for pump start (address = 276)
0x3412 | Combi coil | Set point | Standard | CombiPmpStTmpH | °C | 4x0277 | x.xx | AV288 | 4.22 | 500 | 3000 | 1000 | Combi coil Start temperature for circulation pump of Combi coil ONLY used if CombiPumpFunc (Address 275) = 2 Pump runs if outdoor temp. is < temp. setpoint for pump start | Kombiflade Starttemperatur for Cirk.pumpe på kombiflade Bruges KUN sammen med CombiPumpFunc (reg 4x0276) = 2 Pumpe kører når Udetemperatur < Temp. Setpunkt Pumpe Start | Combi coil Start temperature for circulation pump of Combi coil ONLY used if CombiPumpFunc (Address 275) = 2 Pump runs if outdoor temp. is < temp. setpoint for pump start
0x341C | Combi coil | Set point | Standard | CombiPmpStPrc | % | 4x0278 | x.xx | AV289 | 4.22 | 0 | 10000 | 300 | Combi coil - Start circulation pump with %-open valve ONLY used if CombiPumpFunc (Address 275) = 1 The pump starts when the value is exceeded. | Kombiflade - Start cirkulationspumpe ved %-åben ventil. Bruges KUN sammen med CombiPumpFunc (reg 4x0276) = 1 Pumpen starter når værdien overskrides. | Combi coil - Start circulation pump with %-open valve ONLY used if CombiPumpFunc (Address 275) = 1 The pump starts when the value is exceeded.
0x3413 | Combi coil | Set point |  | CombFrzStopSet | °C | 4x0279 | x.xx | AV290 | 4.22 | 500 | 4000 | 2500 | SetVal for AntiFrost Reg when Agg. = Stop [1/100°C] Heat | Kombiflade - Setpunkt for Anti-Frost Reg når anlægget = Stop [1/100°C] | Combi coil - Setpoint for frost protection control when system is in Stop mode [1/100°C]
0x3414 | Combi coil | Set point |  | CombFrzDrSetH | °C | 4x0280 | x.xx | AV291 | 4.22 | 200 | 2000 | 500 | SetVal for AntiFrost Reg when Agg. = Drift [1/100°C] Heat | Kombiflade - Setpunkt for Anti-Frost Reg når anlægget = Drift [1/100°C] | Combi coil - Setpoint for frost protection control when system is in Operating mode [1/100°C]
0x3415 | Combi coil | Control | Standard | CombiFrzPB | °C | 4x0281 | x.xx | AV292 | 4.22 | 200 | 2000 | 500 | P-Band for AntiFrost Reg [1/100°C] | Kombiflade - P-Bånd for AntiFrost Reg [1/100°C] | Combi coil - P-band for frost protection control [1/100°C]
0x3416 | Combi coil | Set point | Standard | CombiFrzAlHSet | °C | 4x0282 | x.xx | AV293 | 4.22 | 200 | 2000 | 200 | SetVal for AntiFrost TempAlarm [1/100°C] | Kombiflade - Setpunkt for Anti-Frost Temp. Alarm [1/100°C] | Combi coil - Setpoint for frost protection temperature alarm [1/100°C]
0x3925 | Heat exchanger | Set point | Standard | BattEXCFrzStop | °C | 4x0283 | x.xx | AV219 | x.xx | -1000 | 4000 | 2500 | SetVal for AntiFrost Reg when Agg. = Stop [1/100°C] | Væskekoblet flade - Setpunkt for Anti-Frost Reg når anlægget = Stop [1/100°C] | Fluid-coupled coil - Setpoint for frost protection control when unit is in STOP mode [1/100°C]
0x3926 | Heat exchanger | Set point | Standard | BattEXCFrzDrf | °C | 4x0284 | x.xx | AV220 | x.xx | -1000 | 2000 | 500 | SetVal for AntiFrost Reg when Agg. = Drift [1/100°C] | Væskekoblet flade - Setpunkt for Anti-Frost Reg når anlægget = Drift [1/100°C] | Fluid-coupled coil - Setpoint for frost protection control when unit is in OPERATING mode [1/100°C]
0x3927 | Heat exchanger | Control | Standard | BattEXCFrzePB | °C | 4x0285 | x.xx | AV221 | x.xx | 200 | 2000 | 500 | P-Band for AntiFrost Reg [1/100°C] | Væskekoblet flade - P-Bånd for AntiFrost Reg [1/100°C] | Fluid-coupled coil - P-band for frost protection control [1/100°C]
0x3928 | Heat exchanger | Set point | Standard | BattEXCFrzASet | °C | 4x0286 | x.xx | AV222 | x.xx | -1000 | 2000 | 200 | SetVal for AntiFrost TempAlarm [1/100°C] | Væskekoblet flade - Setpunkt for Anti-Frost Temp. Alarm G293 | Fluid-coupled coil - Setpoint for frost protection temperature alarm [1/100°C]
0x23A7 | Combi coil | Current value | Standard | CombiBattTemp | °C | 4x0287 | x.xx | NA | NA | -4000 | 10000 |  | Current HeatWaterCoilTemp [1/100°C] | Kombiflade - Aktuel returtemperatur [1/100°C] | Combi coil - Actual return temperature [1/100°C]
0x33DA | Heating coil, Water | Control | Special | HW12VDCOutFunc |  | 4x0288 | x.xx | AV225 | x.xx | 0 | 1 | 0 | HeatWater VDC out function(Out 12): 0->0-10V, 1->2-10V | Spec. kundevariant: Varmeflade udgang (1,2) VDC out (Out 12): Ventimotortype 0->0-10V, 1->2-10V | Only special customer code: Heat coil 1, step2 output (Out 1,2): Valve actuator type 0->0-10V, 1->2-10V
0x2418 | Heating coil 12 | Set point | Special | HW12_VDCOut | mV | 4x0289 | x.xx | NA | NA | 0 | 10000 |  | Voltage level, HWB1 Out2 | Spec. kundevariant: Varmeflade udgang (1,2) VDC out | Only special customer code: Heat coil 1, step2 output (1,2) VDC out
0x34F2 | Heating coil 12 | Set point | Special | Ht2LimitTyp |  | 4x0290 | x.xx | AV229 | x.xx | 0 | 2 | 0 | Heat2 limiting type 1Room, 2 Outdoor | Spec. kundevariant: Varme2 begrænsning type 1=Rum, 2=Udetemp. | Only special customer code: Heat2 limiting type 1Room, 2 Outdoor
0x34F3 | Heating coil 12 | Set point | Special | Ht2StLimRTemp | °C | 4x0291 | x.xx | AV230 | x.xx | -500 | 0 | -200 | Startdifference temperature | Spec. kundevariant: Startdifference temperatur | Only special customer code: Startdifference temperature [1/100°C]
0x34F4 | Heating coil 12 | Set point | Special | Ht2StLimRPer | % | 4x0292 | x.xx | AV231 | x.xx | 1000 | 10000 | 2000 | Stepsize limiting roomtemp | Spec. kundevariant: Stepvis begrænsning rumtemp | Only special customer code: Stepsize limiting roomtemp [1/100%]
0x34F5 | Heating coil 12 | Set point | Special | Ht2StLimOTemp | °C | 4x0293 | x.xx | AV232 | x.xx | -2000 | 2000 | -500 | Blocking of Heat2 Outdoortemp | Spec. kundevariant: Blokkering af Varme2 i f.t. udetemperatur | Only special customer code: Blocking of Heat2 Outdoortemp [1/100°C]
0x34F6 | Heating coil 12 | Set point | Special | Ht2SetDelTime | Sec | 4x0294 | x.xx | AV234 | x.xx | 0 | 7200 | 3600 | Timeset delayed Heat 2 | Spec. kundevariant: Timeset forsinket Heat 2 | Only special customer code: Timeset delayed Heat 2 [Sec]
0x34F7 | Heating coil 12 | Set point | Special | Ht2FlowOffset | % | 4x0295 | x.xx | AV233 | x.xx | -5000 | 5000 | 5000 | Offset in % of Flow if Heat2 is on | Spec. kundevariant: in % af Flow når Varme2 er on | Only special customer code: in % of Flow if Heat2 is on [1/100%]
0x34F1 | Cooling coil | Set point | Special | NO_CStopRTemp | °C | 4x0296 | x.xx | AV228 | x.xx | 0 | 3000 | 2300 | Stop cooling over roomtemperature | Spec. kundevariant: Stop køling over rumtemperatur | Only special customer code: Stop cooling over roomtemperature [1/100°C]
0x3A8E | Cooling coil | Set point | Special | REXDeIcePerc |  | 4x0297 | x.xx | AV226 | x.xx | 3000 | 10000 | 5000 | Pressure percent over calibration | Spec. kundevariant: Tryk procent over kalibrering | Only special customer code: Pressure percent over calibration
0x34F0 | Cooling coil | Set point | Special | NO_FAirCoolBlk | °C | 4x0298 | x.xx | AV227 | x.xx | -4000 | 2000 | 1000 | Stop temperature freshair cooling | Spec. kundevariant: Stop temperatur udeluftkøling | Only special customer code: Stop temperature freshair cooling [1/100°C]
0x3488 | Humidity | Set point | Standard | DehumSet_RH |  | 4x0299 | x.xx | AV250 | x.xx | 1000 | 10000 | 7000 | Setpoint % Humidity Extract RH, Dehumidity | Setpunkt for affugtning [1/100%rH] | Set point %rH dehumification [1/100%]
0x34F8 | Damper, Recirculation | Control | Special | RecFlowShift |  | 4x0300 | x.xx | AV235 | x.xx | 0 | 2 | 0 | Set Change Airflow Recirce | Spec. kundevariant: Indstil ændring Airflow recirkulation | Only special customer code: Set Change Airflow Recirce
0x34F9 | Damper, Recirculation | Set point | Special | RecClosDStTemp | °C | 4x0301 | x.xx | AV236 | x.xx | -1000 | 2000 | 0 | Temperature for start with open damper | Spec. kundevariant: Temperatur for start med åben spjæld | Only special customer code: Temperature for start with open damper [1/100°C]
0x3A9E | Damper, Recirculation | Alarm | Special | REXAlrLPrcFrz | % | 4x0302 | x.xx | AV308 | 6.41 | 0 | 20000 | 12000 | Alarmlevel in percent if froozen | Spec. kundevariant: Alarmniveau i % ved tilisning [1/100%] | Only special customer code: Alarmlevel in percent if froozen [1/100%]
0x3A9F | Damper, Recirculation | Alarm | Special | REXAlrLPrcDus | % | 4x0303 | x.xx | AV307 | 6.41 | 0 | 10000 | 2000 | Alarmlevel in percent, if dusty | Spec. kundevariant: Alarmniveau i %, ved tilsmudset veksler [1/100%] | Only special customer code: Alarmlevel in percent, if dusty[1/100%]
| AHU controller | Set point | Special | NightSetBack | °C | 4x0013 | 6.51 | AV306 | 6.41 | 0 | 2000 | 0 |  |  | Only special customer code: Night setback [1/100°C]
0x33DB | Heating coil, Water | Control | Special | HW1RiseT100 | Sec | 4x0304 | x.xx | AV305 | NA | 120 | 7200 | 3600 | Risetime 0..100%, in sec | Spec. kundevariant: Stigetid 0..100%, i sek. | Only special customer code: Risetime 0..100%, in sec [Sec]
0x32F5 | Cooling, DX | Set point | Special | ROHRiseT100 | Sec | 4x0305 | x.xx | AV237 | x.xx | 120 | 7200 | 3600 | Timeset for CO2 DX-Cooling-Aggregate from 0 ..100% | Spec. kundevariant: Timeset for CO2 DX-Cooling-Aggregate from 0 ..100% | Only special customer code: Timeset for CO2 DX-Cooling-Aggregate from 0 ..100% [Sec]
0x33C8 | AHU controller | Summer Night Cooling | Standard | SNSupCoolFlw | l/s | 4x0306 | x.xx | AV238 | x.xx | 0 | 32000 | 2000 | SummerNight Motor percent Set when StartDelay is used (Start for Ext/Out -Temp Test) | Setpunkt tilluft luftmængde sommernat køling | Setpoint supply air volume sommernight cooling
0x33C9 | AHU controller | Summer Night Cooling | Standard | SNExtCoolFlw | l/s | 4x0307 | x.xx | AV239 | x.xx | 0 | 32000 | 2000 | SummerNight Motor percent Set when StartDelay is used (Start for Ext/Out -Temp Test) | Setpunkt fraluft luftmængde sommernat køling [m3/h] | Setpoint extract air volume sommernight cooling [m3/h]
0x33CA | AHU controller | Summer Night Cooling | Standard | SNSupCoolPa | Pa | 4x0308 | x.xx | AV240 | x.xx | 0 | 5000 | 50 | SummerNight Motor percent Set when StartDelay is used (Start for Ext/Out -Temp Test) | Setpunkt tilluft tryk sommernat køling [Pa] | Setpoint supply air pressure sommernight cooling [Pa]
0x33CB | AHU controller | Summer Night Cooling | Standard | SNExtCoolPa | Pa | 4x0309 | x.xx | AV241 | x.xx | 0 | 5000 | 50 | SummerNight Motor percent Set when StartDelay is used (Start for Ext/Out -Temp Test) | Setpunkt fraluft tryk sommernat køling [Pa] | Setpoint extract air pressure sommernight cooling [Pa]
0x33CC | AHU controller | Summer Night Cooling | Standard | SNSupCoolPrc | % | 4x0310 | x.xx | AV242 | x.xx | 0 | 10000 | 2000 | SummerNight Motor percent Set when StartDelay is used (Start for Ext/Out -Temp Test) | Setpunkt tilluft fasthastighed sommernat køling[1/100%] | Setpoint supply air constant speed sommernight cooling [1/100%]
0x33CD | AHU controller | Summer Night Cooling | Standard | SNExtCoolPrc | % | 4x0311 | x.xx | AV243 | x.xx | 0 | 10000 | 2000 | SummerNight Motor percent Set when StartDelay is used (Start for Ext/Out -Temp Test) | Setpunkt fraluft fasthastighed sommernat køling[1/100%] | Setpoint extract air constant speed sommernight cooling [1/100%]
0x33CE | AHU controller | Summer Night Cooling | Standard | SNSlvOffsPrc | % | 4x0312 | x.xx | AV247 | x.xx | -5000 | 5000 | 0 |  | Sommernat slave offset [1/100%] | Sommernight cooling slave offset [1/100%]
|  |  | Standard | DewCoolPower | % | 4x0313 | 5.07 | AV294 | 5.07 | 0 | 10000 |  |  |  | Max % CoolPower for Dehumidity without DewPointSensor
0x345B | CO2 sensor | Set point | Special | CO2_MaxModRec | ppm | 4x0314 | x.xx | AV248 | x.xx | 0 | 10000 | 1000 | CO2 Max Value Mod Rec/Rema1000 Mode | Spec. Kundevariant: Max CO2 (butiksmode) [ppm] | Only special customer code: Max CO2 (Store mode) [ppm]
0x345C | CO2 sensor | Set point | Special | CO2_MinModRec | ppm | 4x0315 | x.xx | AV249 | x.xx | 0 | 10000 | 1000 | CO2 Min Value Mod Rec/Rema1000 Mode | Spec. Kundevariant: Min CO2 (butiksmode) [ppm] | Only special customer code: Min CO2 (Store mode) [ppm]
0x3123 | Fan | Set point | Standard | SupMedSpeedSet | l/s | 4x0320 | x.xx | AV251 | x.xx | 0 | 30000 | 5000 | User SupplyFlow-MediumSpeedSet [l/s] | Setpunkt tilluft flow-medium hastighed [l/s] or [m3/h] or [CFM] (Depending on the unit selection in the OJ-Air2Master) | Setpoint supply air flow - medium speed [l/s] or [m3/h] or [CFM] (Depending on the unit selection in the OJ-Air2Master)
0x3223 | Fan | Set point | Standard | ExtMedSpeedSet | l/s | 4x0321 | x.xx | AV254 | x.xx | 0 | 30000 | 5000 | User ExtractFlow-MediumSpeedSet [l/s] | Setpunkt fraluft flow-medium hastighed [l/s] or [m3/h] or [CFM] (Depending on the unit selection in the OJ-Air2Master) | Setpoint exhaust air flow - medium speed [l/s] or [m3/h] or [CFM] (Depending on the unit selection in the OJ-Air2Master)
0x316D | Pressure | Set point | Standard | SupDuctPaMeSet | Pa | 4x0322 | x.xx | AV252 | x.xx | 0 | 5000 | 120 | MediumSpeed DuctPressure Set [Pa] | Setpunkt for kanaltryk Medium tilluft [Pa] | Setpoint supply air duct pressure medium speed [Pa]
0x326D | Pressure | Set point | Standard | ExtDuctPaMeSet | Pa | 4x0323 | x.xx | AV255 | x.xx | 0 | 5000 | 120 | MediumSpeed DuctPressure Set [Pa] | Setpunkt for kanaltryk Medium fraluft [Pa] | Setpoint exhaust air duct pressure medium speed [Pa]
0x346C | CO2 sensor | Set point | Standard | CO2_UserSetMP | ppm | 4x0324 | x.xx | AV256 | x.xx | 0 | 10000 | 1000 | CO2 Regulator User SetPoint for Medium timer Periode(Med CO2 Val) [ppm] | CO2 regulator Setpunkt for medium periode (HI CO2 Val) [ppm] | CO2 controller setpoint medium speed (HI CO2 Val) [ppm]
0x33ED | Damper, Recirculation | Set point | Standard | RecMinFresh | % | 4x0325 | x.xx | AV257 | x.xx | 0 | 10000 | 1000 | Min FreshAir part | Setpunkt minimum friskluft; Kun ved tilvalgt moduleret omluft [1/100%] | Setpoint minimum fresh air; Only if modulated recirculation is selected [1/100%]
0x339C | Filter | Alarm | Standard | FiltExt2StaAlr | Pa | 4x0326 | 4.18 | AV259 | 4.18 | 10 | 500 | 80 | Filter Pressure Alr Limit for ExtFilter2 (static mode) | Fraluft Filter2 Filtertryk Alarmgrænse for (statisk) | Filter Pressure Alr Limit for ExtFilter2 (static mode)
0x339D | Filter | Alarm | Standard | FiltSup2DynAlr | % | 4x0327 | 4.18 | AV260 | 4.18 | 1000 | 10000 | 5000 | Filter Pressure Alr Limit for SupFilter (dynamic mode) | Tilluft Filter Filtertryk Alarmgrænse for (statisk) | Filter Pressure Alr Limit for SupFilter (dynamic mode)
0x339E | Filter | Alarm | Standard | FiltExt2DynAlr | % | 4x0328 | 4.18 | AV261 | 4.18 | 1000 | 10000 | 5000 | Filter Pressure Alr Limit for ExtFilter (dynamic mode) | Fraluft Filter Filtertryk Alarmgrænse for (statisk) | Filter Pressure Alr Limit for ExtFilter (dynamic mode)
| Zone 1 | Set point | Standard | ZM1_RoomTmpSet |  | 4x0329 | 4.19 | AV262 | 4.19 | -4000 | 10000 |  |  |  | ZoneModule 1 - Room Temperature Setpoint
| Zone 1 | Set point | Standard | ZM1_MinSupTemp |  | 4x0330 | 4.19 | AV263 | 4.19 | -4000 | 10000 |  |  |  | ZoneModule 1 - Minimum Supply Temperature
| Zone 1 | Set point | Standard | ZM1_MaxSupTemp |  | 4x0331 | 4.19 | AV264 | 4.19 | -4000 | 10000 |  |  |  | ZoneModule 1 - Maximum Supply Temperature
| Zone 1 | Set point | Standard | ZM1_CO2Set |  | 4x0332 | 4.19 | AV265 | 4.19 | 0 | 5000 |  |  |  | ZoneModule 1 - Room CO2 Setpoint
| Zone 1 | Set point | Standard | ZM1_RHSet |  | 4x0333 | 4.19 | AV266 | 4.19 | 0 | 10000 |  |  |  | ZoneModule 1 - Room RH Setpoint
| Zone 1 | Set point | Standard | ZM1_PIRMinFlow |  | 4x0334 | 4.19 | AV267 | 4.19 | 0 | 0 |  |  |  | ZoneModule 1 - VAV Supply PIR Min Air Flow
| Zone 2 | Set point | Standard | ZM2_RoomTmpSet |  | 4x0335 | 4.19 | AV268 | 4.19 | -4000 | 10000 |  |  |  | ZoneModule 2 - Room Temperature Setpoint
| Zone 2 | Set point | Standard | ZM2_MinSupTemp |  | 4x0336 | 4.19 | AV269 | 4.19 | -4000 | 10000 |  |  |  | ZoneModule 2 - Minimum Supply Temperature
| Zone 2 | Set point | Standard | ZM2_MaxSupTemp |  | 4x0337 | 4.19 | AV270 | 4.19 | -4000 | 10000 |  |  |  | ZoneModule 2 - Maximum Supply Temperature
| Zone 2 | Set point | Standard | ZM2_CO2Set |  | 4x0338 | 4.19 | AV271 | 4.19 | 0 | 5000 |  |  |  | ZoneModule 2 - Room CO2 Setpoint
| Zone 2 | Set point | Standard | ZM2_RHSet |  | 4x0339 | 4.19 | AV272 | 4.19 | 0 | 10000 |  |  |  | ZoneModule 2 - Room RH Setpoint
| Zone 2 | Set point | Standard | ZM2_PIRMinFlow |  | 4x0340 | 4.19 | AV273 | 4.19 | 0 | 0 |  |  |  | ZoneModule 2 - VAV Supply PIR Min Air Flow
| Zone 3 | Set point | Standard | ZM3_RoomTmpSet |  | 4x0341 | 4.19 | AV274 | 4.19 | -4000 | 10000 |  |  |  | ZoneModule 3 - Room Temperature Setpoint
| Zone 3 | Set point | Standard | ZM3_MinSupTemp |  | 4x0342 | 4.19 | AV275 | 4.19 | -4000 | 10000 |  |  |  | ZoneModule 3 - Minimum Supply Temperature
| Zone 3 | Set point | Standard | ZM3_MaxSupTemp |  | 4x0343 | 4.19 | AV276 | 4.19 | -4000 | 10000 |  |  |  | ZoneModule 3 - Maximum Supply Temperature
| Zone 3 | Set point | Standard | ZM3_CO2Set |  | 4x0344 | 4.19 | AV277 | 4.19 | 0 | 5000 |  |  |  | ZoneModule 3 - Room CO2 Setpoint
| Zone 3 | Set point | Standard | ZM3_RHSet |  | 4x0345 | 4.19 | AV278 | 4.19 | 0 | 10000 |  |  |  | ZoneModule 3 - Room RH Setpoint
| Zone 3 | Set point | Standard | ZM3_PIRMinFlow |  | 4x0346 | 4.19 | AV279 | 4.19 | 0 | 0 |  |  |  | ZoneModule 3 - VAV Supply PIR Min Air Flow
| Zone 4 | Set point | Standard | ZM4_RoomTmpSet |  | 4x0347 | 4.19 | AV280 | 4.19 | -4000 | 10000 |  |  |  | ZoneModule 4 - Room Temperature Setpoint
| Zone 4 | Set point | Standard | ZM4_MinSupTemp |  | 4x0348 | 4.19 | AV281 | 4.19 | -4000 | 10000 |  |  |  | ZoneModule 4 - Minimum Supply Temperature
| Zone 4 | Set point | Standard | ZM4_MaxSupTemp |  | 4x0349 | 4.19 | AV282 | 4.19 | -4000 | 10000 |  |  |  | ZoneModule 4 - Maximum Supply Temperature
| Zone 4 | Set point | Standard | ZM4_CO2Set |  | 4x0350 | 4.19 | AV283 | 4.19 | 0 | 5000 |  |  |  | ZoneModule 4 - Room CO2 Setpoint
| Zone 4 | Set point | Standard | ZM4_RHSet |  | 4x0351 | 4.19 | AV284 | 4.19 | 0 | 10000 |  |  |  | ZoneModule 4 - Room RH Setpoint
| Zone 4 | Set point | Standard | ZM4_PIRMinFlow |  | 4x0352 | 4.19 | AV285 | 4.19 | 0 | 0 |  |  |  | ZoneModule 4 - VAV Supply PIR Min Air Flow
| Fan | Set point | Standard | SupFixMePrcSet |  | 4x0353 | 6.10 | AV253 | 6.10 | 100 | 10000 | 3500 |  |  | Supply Motor Mediumspeed [1/100%], Fixed Fan Speed
| Fan | Set point | Standard | SupFixLoPrcSet |  | 4x0354 | 6.10 | AV299 | 6.10 | 100 | 10000 | 2500 |  |  | Supply Motor Lowspeed [1/100%], Fixed Fan Speed
| Fan | Set point | Standard | SupFixHiPrcSet |  | 4x0355 | 6.10 | AV300 | 6.10 | 100 | 10000 | 5000 |  |  | Supply Motor Highspeed [1/100%], Fixed Fan Speed
| Fan | Set point | Standard | ExtFixMePrcSet |  | 4x0356 | 6.10 | AV301 | 6.10 | 100 | 10000 | 3500 |  |  | Extract Motor Mediumspeed [1/100%], Fixed Fan Speed
| Fan | Set point | Standard | ExtFixLoPrcSet |  | 4x0357 | 6.10 | AV302 | 6.10 | 100 | 10000 | 2500 |  |  | Extract Motor Lowspeed [1/100%], Fixed Fan Speed
| Fan | Set point | Standard | ExtFixHiPrcSet |  | 4x0358 | 6.10 | AV303 | 6.10 | 100 | 10000 | 5000 |  |  | Extract Motor Highspeed [1/100%], Fixed Fan Speed
| Damper, Recirculation | Set point | Standard | RecMaxFresh |  | 4x0359 | 6.10 | AV304 | 6.10 | 3000 | 10000 | 10000 |  |  | Max FreshAir part [1/100%]
| AHU controller | Set point | Special | ROHOutdBlkTmp |  | 4x0360 | 6.41 | AV319 | 6.41 | -2000 | 5000 | -500 |  |  | Heat 2 blocked over this Temperatur (Special Cust. Code only)
0x3009 | AHU controller | Control | Standard | BMSDrfCtrlReg |  | 4x0500 | x.xx | AV244 | x.xx | 0 | 1000 |  | Register for BMS-Driftmode | 11 = BMS stop 105 = BMS lavfart 210 = BMS højfart 414 = BMS medium speed 211 = BMS sommernatskøling 220 = BMS natopvarmning (recirkulation) Bemærk BMS-driftmodes er kun tilgænge efter aktivering af fysisk indgang "Driftmode via BMS system" | 11 = BMS stop 105 = BMS low speed 210 = BMS high speed 211 = BMS sommernight cooling 220 = BMS night heating mode (Recirculation) 414 = BMS medium speed BMS-modes only avalable after activation of physical input "Operating mode via BMS"
0x327D | Temp. out door | Current value | Standard | MBT_OutDoor | °C | 4x0501 | x.xx | AV245 | x.xx | -6000 | 10000 |  | Current external Modbus OutDoorTemp [1/100°C] | BMS udetemperatur [1/100°C] | BMS outdoor temperatur [1/100°C]
0x327E | Temp. room | Current value | Standard | MBT_Room1 | °C | 4x0502 | x.xx | AV246 | x.xx | -4000 | 10000 |  | Current external Modbus RoomTemp [1/100°C] | BMS rumtemperatur [1/100°C] | BMS room temperatur [1/100°C]
Note on B3: Jens B. Antonsen: Modbus and BACnet parameters reflect current values on installed components in the actual AHU. The parameters are always present, but might not be active. Actual AHU components installed depends on the AHU manufacturer brand and model.
Note on D3: Jens B. Antonsen: Standard: Always included in OJ-Air2master. Special: Partly included in some private label variants. Check the AHU controller part. No. and the AHU manufactor documentation.
Note on G3: Jens B. Antonsen: Registers start at no. 1. Adresses start at no. 0. A typical mistake is R/W to a neighbour register.
Note on G495: Jens B. Antonsen: Available as 3x0012
Note on G496: Jens B. Antonsen: Availlable as 3x0013
Note on G504: Jens B. Antonsen: Available as 4x0289
Note on G565: Jens B. Antonsen: Available as 4x0287
Note on H3: Jens B. Antonsen: Number: Register is available in this software version and higher versions. x.xx: Register is available in this software and some lower versions.
Note on I495: Jens B. Antonsen: Equal to AI10
Note on I496: Jens B. Antonsen: Equal to AI11
Note on I709: Jens B. Antonsen: Equal to AV14
Note on I710: Jens B. Antonsen: Equal to AV14
Note on I947: Jens B. Antonsen: Available as AI126
Note on I949: Jens B. Antonsen: Available as AI109
Note on J3: Jens B. Antonsen: Number: Parameter is available in this software version and higher versions. x.xx: Parameter is available in this software and some lower versions.
Note on K3: Jens B. Antonsen: Minimum value. Lower values will be ignored.
Note on L3: Jens B. Antonsen: Maximum value. Higher values will be ignored.
Note on M3: Jens B. Antonsen: Default valule from OJ Electronics factory.