## Info
© 2023 OJ Electronics A/S · ® The OJ trademark is a registered trademark belonging to OJ Electronics A/S
OJ-AHC-3000
Modbus protocol
Software version 2.10
Quick overview
The most common used parameters.
Modbus Info
General information about modbus RTU/TCP-IP
Modbus RTU Connection
How to connect Modbus RTU (RS-485)
Parameters
Complete list of all Modbus parameters.

## Quick overview
Modbus overview
Quick overview over the most used parameters |  |  |  |  | Exhaust | Modbus
[5 empty] | Current exhaust air temp. [1/100°C] | 3x0031 | R
[5 empty] | Current extract flow [l/s] | 3x0009 | R
[5 empty] | Extract air motor output percentage (OJ-DV) [1/100%] | 3x0014 | R
[5 empty] | Setpoint for extract flow, low speed [l/s] | 4x0019 | RW
[5 empty] | Setpoint for extract flow, medium speed [l/s] | 4x0020 | RW
[5 empty] | Setpoint for extract flow, high speed [l/s] | 4x0021 | RW
[5 empty] | Heat Exchanger | Modbus
[5 empty] | Heat exchanger (Cross & Counter flow/3. part) (0-10V) – output percent. [%] | 3x0046 | R
[5 empty] | Outdoor air | Modbus
[5 empty] | Current outdoor temp. (AHU internal sensor) [1/100°C] | 3x0029 | R
[5 empty] | Outdoor air filter; current pressure drop [Pa] | 3x0038 | R
[5 empty] | Extract | Modbus
[5 empty] | Current extract air temperature [1/100°C] | 3x0027 | R
[5 empty] | Extract air filter; current pressure drop [Pa] | 3x0037 | R
[5 empty] | Current CO2 value [ppm] (0-10V=0-2000ppm) | 3x0011 | R
[5 empty] | Current VOC value from the VOC sensor (VTH-6202) | 3x0012 | R
[5 empty] | Current humidity value from the humidity sensor (HTH-6202) [1/100°C | 3x0171 | R
[5 empty] | Current room temperature [1/100 °C] | 3x0030 | R
[5 empty] | Current extract duct pressure [Pa] | 3x0005 | R
[5 empty] | Setpoint for duct pressure, extract, low speed [Pa] | 4x0010 | RW
[5 empty] | Setpoint for duct pressure, extract, medium speed [Pa] | 4x0011 | RW
[5 empty] | Setpoint for duct pressure, extract, high speed [Pa] | 4x0012 | RW
[5 empty] | Supply | Modbus
[5 empty] | Current supply air temperature [1/100°C] | 3x0025 | R
[5 empty] | Select temperature control mode; 1=Supply, 2=Extract, 3=Room | 4x0090 | RW
[5 empty] | Temperature setpoint for control mode: Supply air temperature [1/100°C] | 4x0091 | RW
[5 empty] | Temperature setpoint for control mode: Extract temperature [1/100°C] | 4x0092 | RW
[5 empty] | Temperature setpoint for control mode: Room temperature [1/100°C] | 4x0093 | RW
[5 empty] | Min. limit, supply air temp. [1/100°C] | 4x0094 | RW
[5 empty] | Max. limit, supply air temp. [1/100°C] | 4x0095 | RW
|  | Controls | Modbus |  | Current heating power [1/100%] | 3x0047 | R
|  | Current operating mode | 3x0001 | R | Heating relay 1 | 1x0031 | R
|  | Operation ON/OFF | 1x0001 | R | Current heating coil temp. (Return pipe sensor) [1/100°C] | 3x0034 | R
|  | Extended high speed (Boost) –> Active | 1x0005 | R | Current cooling power [1/100%] | 3x0048 | R
|  | Minimum one A-alarm triggered | 1x0033 | R | Supply air motor output percentage (OJ-DV) [1/100%] | 3x0013 | R
|  | Minimum one B-alarm triggered | 1x0034 | R | Current supply flow [l/s] | 3x0007 | R
|  | Alarm reset signal (AutoReturn to zero) | 0x0001 | RW | Setpoint for supply flow, low speed [l/s] | 4x0015 | RW
[5 empty] | Setpoint for supply flow, medium speed [l/s] | 4x0016 | RW
[5 empty] | Setpoint for supply flow, high speed [l/s] | 4x0017 | RW
[5 empty] | Current supply duct pressure [Pa] | 3x0003 | R
[5 empty] | Setpoint for supply duct pressure, low speed [Pa] | 4x0004 | RW
[5 empty] | Setpoint for supply duct pressure, medium speed [Pa] | 4x0005 | RW
[5 empty] | Setpoint for supply duct pressure, high speed [Pa] | 4x0006 | RW
R=Read only
RW=Read & Write
© 2023 OJ Electronics A/S · ® The OJ trademark is a registered trademark belonging to OJ Electronics A/S

## Modbus info
Modbus RTU/TCP-IP
OJ-AHC-3000-T/-B, Program version 1.00 and later versions
Overview
This Protocol contains all Modbus addresses and registers in the OJ-AHC-3000 controller.
Updating of values in the individual registers is dependent on the actual configuration of the air handling unit.
It will, for example, be possible to read out water heating coil temperature (Register 3x0034) irrespective of
whether or not an water heating coil is installed in the system concerned.
In the SW the value will, however, only be used if the water heating coil and the temperature sensor is installed.
Modbus can access single addresses or several addresses simultaneously,
either reading or writing 1-bit or 16-bit values.
A Modbus address contains either a 1-bit value or a 16-bit integer.
Communication ports
TCP/IP: 1 x 10/100 Mbit Ethernet, RJ45 connector, Single user connection
BMS (RS485): 1 x external Modbus, RS485, RJ12 connector, which can be set for 9.6 kBaud, 19.2 kBaud or 38.4 kBaud.
RJ12Connections: Pin1: NC, Pin2: GND, Pin3: RS485 B, Pin4: RS485 A, Pin5: NC, Pin6: GND (NC=Not connected)
Standard Modbus TCP/IP Communikation port: 502 - Single user connection. New connection interrupt connected user.
IP-address: 192.168.1.100 (Static)*
Netmask: 255.255.255.0*
*=Factory settings
Modbus data format
Modbus data types are 1-bit values and 16-bit values.
Modbus Type |  | Description | Reference
Coil Status (R/W) |  | Discrete Output | 0x
Input Status (R) |  | Discrete Input | 1x
Holding Register (R/W) |  | 16-bit Output Register | 4x
Input register (R) |  | 16-bit Input Register | 3x
R = Read Only
R/W = Read / Write
Supported Modbus commands
OJ Air2 supports the following Modbus commands:
Function code | Description
1 | Read Coil Status
2 | Read Input Status
3 | Read Holding Registers
4 | Read Input Registers
5 | Force Single Coil
6 | Preset Single Registers
8 | Diagnostics. Sub-function 00 Only - Return Query Data (loop back)
15 | Force Multiple Coils
16 | Preset Multiple Registers
© 2023 OJ Electronics A/S · ® The OJ trademark is a registered trademark belonging to OJ Electronics A/S

## Modbus Overview parameters (hidden)
Actual extract flow [l/s] |  |  | 3x0009
Extract motor output percentage [1/100%] |  |  | 3x0083 |  |  |  | Actual operating mode | 3x0001
Setpoint for extract flow, low speed [l/s] |  |  | 4x0014 |  |  |  | Operation ON/OFF | 1x0001
Setpoint for extract flow, high speed [l/s] |  |  | 4x0015 |  |  |  | Extended low speed –> Active | 1x0004
[7 empty] | Extended high speed –> Active | 1x0005
|  | Actual extract duct pressure [Pa] |  | 3x0005 |  |  | Alarm relay 1 (A-alarm) | 1x0035
|  | Setpoint for duct pressure, extract, low speed [Pa] |  | 4x0007 |  |  | Alarm relay 2 (B-alarm) | 1x0036
|  | Setpoint for duct pressure, extract, high speed [Pa] |  | 4x0008 |  |  | Alarm reset signal (AutoReturn to zero) | 0x0001
|  | Inlet filter pressure [Pa] |  | 3x0031
|  | Inlet filter monitor max. alarm limit [Pa] |  | 3x0039
[7 empty] | Actual inlet temperature [1/100°C] | 3x0020
[7 empty] | Control type setting | 4x0148
[7 empty] | Temperature setpoint for actual control type | 4x0149
[7 empty] | Extract filter pressure [Pa] | 3x0032
[7 empty] | Max. alarm limit, extract filter pressure drop [Pa] | 3x0040
[7 empty] | Actual room temperature [1/100 °C] | 3x0025
[7 empty] | Actual exhaust temp. [1/100°C] | 3x0026
[7 empty] | Min. limit, inlet temp. [1/100°C] | 4x0150
[7 empty] | Max. limit, inlet temp. [1/100°C] | 4x0151
[7 empty] | Actual inlet duct pressure [Pa] | 3x0003
[7 empty] | Setpoint for duct pressure, inlet, low speed [Pa] | 4x0003
[7 empty] | Setpoint for duct pressure, inlet, high speed [Pa] | 4x0004
[7 empty] | Actual inlet flow [l/s] | 3x0007
[7 empty] | Inlet motor output percentage [1/100%] | 3x0073
[7 empty] | Setpoint for inlet flow, low speed [l/s] | 4x0011
[7 empty] | Setpoint for inlet flow, high speed [l/s] | 4x0012
Actual outdoor temp. [1/100°C] 3x0024 |  |  |  |  | Actual heating power [1/100%] | 3x0054
[5 empty] | Heating relay 1 | 1x0031
| Rot. heat exchanger – output percent. [%] |  | 3x0092 |  | Act. heating bat. temp.[1/100°C] | 3x0030
|  |  | Actual cooling power [1/100%] |  | 3x0056
© 2016 OJ Electronics A/S · ® The Trade Mark OJ is an registered Trade Mark belonging to OJ Electronics A/S
06-07-16

## Modbus RTU Connection
© 2023 OJ Electronics A/S · ® The OJ trademark is a registered trademark belonging to OJ Electronics A/S
OJ AHC-3000 Controller
RJ12 Modbus/RTU connection
Fig. 1 OJ-AHC-3000, Connector diagram, visualized from the frontside
Fig. 3 Modbus RTU RJ12 socket
Fig. 2 Configuration for communication via external Modbus
Communication over external Modbus RTU / RS485
- NC
- NC
*- NC = Not Connected

## Parameters
Component | Function | Standard/ Special | Name | SI Unit | Modbus register | SW vers. | Min | Max | English
1. Info | 1. Info | 1. Info | 1. Info |  | Coil status (R/W)
AHU controller | Alarm | Standard | AL_ManResetAll |  | 0x0001 | 1.00 | 0 | 1 | Alarm reset signal (AutoReturn to zero)
AHU controller | Summer Night Cooling | Standard | SN_Func_UserSet |  | 0x0003 | 1.00 | 0 | 1 | Summer night cooling: ON/OFF
1. Info | 1. Info | 1. Info | 1. Info |  | Input status (R) |  | 1. Info | 1. Info
AHU controller | Speed | Standard | IOC_DO_Operation_Set |  | 1x0001 | 1.00 | 0 | 1 | Operation ON/OFF
AHU controller | Speed | Standard | IOC_DI_Ext_Stop_Read |  | 1x0002 | 1.00 | 0 | 1 | External stop
AHU controller | Speed | Standard | IOC_DI_ExtHigh_Read |  | 1x0003 | 1.00 | 0 | 1 | Externalhigh speed
AHU controller | Speed | Standard | AB_Active |  | 1x0005 | 1.00 | 0 | 1 | Extended high speed –> Active (AHC-3000 : Boost)
Electric heating coil | Status | Standard | HT_RH_ReductionActive |  | 1x0010 | 1.00 | 0 | 1 | Power to electric heating coil reduced due to low flow
AHU controller | Summer Night Cooling | Standard | SN_Active |  | 1x0011 | 1.00 | 0 | 1 | Summer night cooling is active
Rotary Heat Exchanger | Speed | Standard | RX_PO_Active |  | 1x0017 | 1.00 | 0 | 1 | Exercising heat exchanger –> Active, (AHC-3000 : periodical operation, PO, DRHX)
Heat Exchanger | Status | Standard | PX_DF_State |  | 1x0018 | 1.00 | 0 | 1 | Signal to cross-flow exchanger reduced (frost protection)
AHU controller | Status | Standard | PR_SA_MaxSpeedActive |  | 1x0020 | 1.00 | 0 | 1 | Supply duct pressure controller increased to max. flow
AHU controller | Status | Standard | PR_EA_MaxSpeedActive |  | 1x0022 | 1.00 | 0 | 1 | Extract duct pressure controller increased to max. flow
AHU controller | Status | Standard | CL_CR_Active |  | 1x0023 | 1.00 | 0 | 1 | Cooling recovery –> status
Water Heating Coil | Status | Standard | HT_RH_FP_RegActive |  | 1x0024 | 1.00 | 0 | 1 | Circulation pump on heating coil: Frost protection –> Active
Water Heating Coil | Status | Standard | HT_RH_PO_Pump_Active |  | 1x0025 | 1.00 | 0 | 1 | Circulation pump on heating coil: Pump exercising –> Active
Water Cooling Coil | Status | Standard | CL_RC_PO_Pump_Active |  | 1x0026 | 1.00 | 0 | 1 | CoolWaterCoil PumpExercise active
AHU controller | Status | Standard | AR_FlowDownActive |  | 1x0027 | 1.00 | 0 | 1 | Signal to heating coil reduced (insufficient flow) –> Active
AHU controller | Status | Standard | TR_SA_MinSupTempAct |  | 1x0028 | 1.00 | 0 | 1 | "1" when min. supply temperature control is active. Only active when TempRegMode is 1 or 2 (room temp. control)
AHU controller | Status | Standard | TR_SA_MaxSupTempAct |  | 1x0029 | 1.00 | 0 | 1 | "1" when max. supply temperature control is active. Only active when TempRegMode is 1 or 2 (room temp. control)
AHU controller | Status | Standard | IOC_DO_HT1_RE1_Set |  | 1x0031 | 1.00 | 0 | 1 | Heating relay 1
AHU controller | Status | Standard | IOC_DO_CL1_RE1_Set |  | 1x0032 | 1.00 | 0 | 1 | Cooling relay 1
AHU controller | Alarm | Standard | AL_Priority_A_Triggered |  | 1x0033 | 1.00 | 0 | 1 | At least one active alarm, A-Alarm >> New in AHC-3000
AHU controller | Alarm | Standard | AL_Priority_B_Triggered |  | 1x0034 | 1.00 | 0 | 1 | At least one active alarm, B-Alarm
AHU controller | Fire | Standard | IOC_DI_Ext_Fire_Read |  | 1x0037 | 1.00 | 0 | 1 | Fire alarm signal (room sensor)
AHU controller | Smoke | Standard | IOC_DI_Ext_Smoke_Read |  | 1x0038 | 1.00 | 0 | 1 | Smoke/fire alarm signal (duct sensor)
AHU controller | Status | Standard | TR_CL_RC_Available |  | 1x0040 | 1.00 | 0 | 1 | Coolsource available
AHU controller | Status | Standard | TR_CL_HX_Available |  | 1x0041 | 1.00 | 0 | 1 | EXC as Coolsource available
AHU controller | Status | Standard | TR_HT_HX_Available |  | 1x0042 | 1.00 | 0 | 1 | EXC as Heatsource available
AHU controller | Status | Standard | TR_HT_RH_Available |  | 1x0043 | 1.00 | 0 | 1 | Heatsource available
AHU controller | Status | Standard | TR_HT_FlowDnRegAvailable |  | 1x0044 | 1.00 | 0 | 1 | Flowdown available
Rotary Heat Exchanger | Status | Standard | DRHX_DriftON |  | 1x0050 | 1.00 | 0 | 1 | Rotary heat exchanger – motor control ON/OFF (only with OJ-RHX2M)
Rotary Heat Exchanger | Alarm | Standard | DRHX_RotorAlr |  | 1x0053 | 1.00 | 0 | 1 | Rotary heat exchanger – rotation alarm (only with OJ-DRHX)
Common Fan, Supply | Alarm | Standard | AH_Common_SA_Fan |  | 1x0055 | 1.00 | 0 | 1 | Common Alarm SA Fan
Common Fan, Supply | Alarm | Standard | AH_Common_SA_FwDu |  | 1x0056 | 1.00 | 0 | 1 | Common Alarm SA Pressure / Flow
Common Fan, Exhaust | Alarm | Standard | AH_Common_EA_Fan |  | 1x0057 | 1.00 | 0 | 1 | Common Alarm EA/EXH Fan
Common Fan, Exhaust | Alarm | Standard | AH_Common_EA_FwDu |  | 1x0058 | 1.00 | 0 | 1 | Common Alarm EA/EXH Pressure / Flow
Common Circulation Pumps | Alarm | Standard | AH_Common_Pumps |  | 1x0059 | 1.00 | 0 | 1 | Common Alarm Circulation Pump
Common Heat Exchanger | Alarm | Standard | AH_Common_RXCX |  | 1x0060 | 1.00 | 0 | 1 | Common Alarm Exchanger
Common Frost | Alarm | Standard | AH_Common_Frost |  | 1x0061 | 1.00 | 0 | 1 | Common Alarm Frost HW/CMB Coil
Common El-Heating-Coil | Alarm | Standard | AH_Common_ElCoil |  | 1x0062 | 1.00 | 0 | 1 | Common Alarm Electric heating coil
Common Temperature | Alarm | Standard | AH_Common_Tmp_H_L |  | 1x0063 | 1.00 | 0 | 1 | Common Alarm temperature high/low
Common Filter, Outdoor | Alarm | Standard | AH_Common_FM_OA |  | 1x0064 | 1.00 | 0 | 1 | Common Alarm OA Filter
Common Filter, Extract | Alarm | Standard | AH_Common_FM_EA |  | 1x0065 | 1.00 | 0 | 1 | Common Alarm EA Filter
Common Temp. Sensors | Alarm | Standard | AH_Common_T_Sensor |  | 1x0066 | 1.00 | 0 | 1 | Common Alarm Temperature Sensors
Common Intern MB | Alarm | Standard | AH_Common_Intern_MB |  | 1x0068 | 1.00 | 0 | 1 | Common Alarm Com. Intern Modbus
Fan, Supply | Status | Standard | BMS_SA_Fan_On |  | 1x0075 | 1.00 | 0 | 1 | Supply motor ON/OFF (0-10V Type)
Fan, Supply | Alarm | Standard | BMS_SA_Fan_Alr_Inp |  | 1x0076 | 1.00 | 0 | 1 | Supply Motor Alarm, Dig. Input (0-10V Type)
Fan, Exhaust | Status | Standard | BMS_EA_Fan_On |  | 1x0080 | 1.00 | 0 | 1 | Extract motor ON/OFF (0-10V Type)
Fan, Exhaust | Alarm | Standard | BMS_EA_Fan_Alr_Inp |  | 1x0081 | 1.00 | 0 | 1 | Extract Motor Alarm, Dig. Input (0-10V Type)
Damper, Outdoor & Exhaust | Status | Standard | IOC_DO_Damper_Set |  | 1x0085 | 1.00 | 0 | 1 | Output for outdoor air/exhaust air active, dig.Out Damper
AHU controller | Status | Standard | IOC_DI_Ext_Start_Read |  | 1x0090 | 1.00 | 0 | 1 | Status external start input
1. Info | 1. Info | 1. Info | 1. Info |  | Input register (R) |  | 1. Info | 1. Info | 1. Info
AHU controller | Control | Standard | OL_AHU_State |  | 3x0001 | 1.00 | 0 | 499 | Actual operating mode 000-099: Unit stopped 100-199: Unit in low speed mode 200-299: Unit in medium speed mode 300-399: Unit in high speed mode 400-499: Unit in spec. control mode
Pressure | Current value | Standard | IOC_PS_SA_DU_Read |  | 3x0003 | 1.00 | 0 | 25000 | Actual supply duct pressure [1/10 Pa]
Pressure | Set point | Standard | PR_SA_Reg_Set |  | 3x0004 | 1.00 | 0 | 7500 | Setpoint for supply duct pressure controller [1/10 Pa]
Pressure | Current value | Standard | IOC_PS_EA_DU_Read |  | 3x0005 | 1.00 | 0 | 25000 | Actual extract duct pressure [1/10 Pa]
Pressure | Set point | Standard | PR_EA_Reg_Set |  | 3x0006 | 1.00 | 0 | 7500 | Setpoint for extract duct pressure controller [1/10 Pa]
Flow | Current value | Standard | SA_Flow |  | 3x0007 | 1.00 | 100 | 30000 | Actual supply flow [l/s]
Flow | Set point | Standard | AR_SA_Reg_Set |  | 3x0008 | 1.00 |  | AR_SA_MS_UserSet | Setpoint for supply flow controller [l/s]
Flow | Current value | Standard | EA_Flow |  | 3x0009 | 1.00 | 100 | 30000 | Actual extract flow [l/s]
Flow | Set point | Standard | AR_EA_Reg_Set |  | 3x0010 | 1.00 | 0 | AR_EA_MS_UserSet | Setpoint for extract flow controller [l/s]
CO2 sensor | Current value | Standard | CO2_SensorSignal |  | 3x0011 | 1.00 | 0 | 2000 | CO2 concentration recorded by CO2 sensor [ppm]
VOC | Current value | Standard | VOC_Level |  | 3x0012 | 1.00 | 0 | 8000 | VOC concentration recorded by VOC sensor [ppm]
Fan, Supply | Current value | Standard | HMI35_SA_Procent |  | 3x0013 | 1.00 | 0 | 10000 | Percent-Output to SA [1/100%], DV / 0-10V
Fan, Exhaust | Current value | Standard | HMI35_EA_Procent |  | 3x0014 | 1.00 | 0 | 10000 | Percent-Output to EA [1/100%], DV / 0-10V
Flow | Set point | Standard | AHU_SA_MaxFlow |  | 3x0017 | 1.00 | 0 | 30000 | Supply FC max. flow [l/s]
Flow | Set point | Standard | AHU_EA_MaxFlow |  | 3x0018 | 1.00 | 0 | 30000 | Extract FC max. flow [l/s]
Temp. Supply | Current value | Standard | AHU_SA_Temp |  | 3x0025 | 1.00 | -5500 | 12500 | Actual supply temperature [1/100°C]
Temp. Supply | Set point | Standard | TR_SA_TempRegSet |  | 3x0026 | 1.00 | 0 | 4000 | Setpoint for supply temperature controller [1/100°C]
Temp. Extract | Current value | Standard | AHU_EA_Temp |  | 3x0027 | 1.00 | -5500 | 12500 | Actual extract temperature [1/100°C]
Temp. Extract | Set point | Standard | TR_EA_TempRegSet |  | 3x0028 | 1.00 | 500 | 4000 | Setpoint for extract temperature controller [1/100°C]
Temp. Outdoor | Current value | Standard | AHU_OA_Temp |  | 3x0029 | 1.00 | -5500 | 12500 | Actual outdoor temperature [1/100°C]
Temp. Room | Current value | Standard | AHU_RM_Temp |  | 3x0030 | 1.00 | 0 | 4000 | Actual room temperature [1/100°C]
Temp. Exhaust | Current value | Standard | AHU_EXH_Temp |  | 3x0031 | 1.00 | -5500 | 12500 | Actual exhaust temperature [1/100°C]
Temp. Heating Coil | Current value | Standard | AHU_HWR_Temp |  | 3x0034 | 1.00 | -5500 | 12500 | Actual heating coil temperature [1/100°C]
Fan, Supply Pressure | Current value | Standard | IOC_PS_SA_FW_Read |  | 3x0035 | 1.00 | 0 | 25000 | Supply Fan pressure [1/10 Pa]
Fan, Extract Pressure | Current value | Standard | IOC_PS_EA_FW_Read |  | 3x0036 | 1.00 | 0 | 25000 | Exhaust Fan pressure [1/10 Pa]
Filter, Extract pressure | Current value | Standard | IOC_PS_SF_EA_FM_Read |  | 3x0037 | 1.00 | 0 | 25000 | Extract filter pressure [1/10 Pa]
Filter, Outdoor pressure | Average value | Standard | IOC_PS_SF_OA_FM_Read |  | 3x0038 | 1.00 | 0 | 25000 | Outdoor filter pressure [1/10 Pa]
AHU controller | Summer Night Cooling | Standard | SN_SecondsOfActiveHeat |  | 3x0045 | 1.00 | 0 | 32000 | SummerNight Time with Heat Demand [sec]
Heat Exchanger | Set point | Standard | HX_HT_PowerRegSet |  | 3x0046 | 1.00 | 0 | 10000 | Heat exchange controller heating power [1/100%]
Heating Coil | Set point | Standard | HT_RH_PowerRegSet |  | 3x0047 | 1.00 | 0 | 10000 | Actual heating power [1/100%]
Cooling Coil | Set point | Standard | CL_RC_PowerRegSet |  | 3x0048 | 1.00 | 0 | 10000 | Cooling controller power [1/100%]
AHU controller | Set point | Standard | HX_CL_PowerRegSet |  | 3x0049 | 1.00 | 0 | 10000 | Cool exchange controller coolting power [1/100%]
Fan, Supply | State of SA Fan | Standard | OL_SA_State |  | 3x0060 | 1.00 | 0 | 499 | Actual operating mode 000-099: Unit stopped 100-199: Unit in low speed mode 200-299: Unit in medium speed mode 300-399: Unit in high speed mode 400-499: Unit in spec. control mode
Fan, Exhaust | State of EA Fan | Standard | OL_EA_State |  | 3x0061 | 1.00 | 0 | 499 | Actual operating mode 000-099: Unit stopped 100-199: Unit in low speed mode 200-299: Unit in medium speed mode 300-399: Unit in high speed mode 400-499: Unit in spec. control mode
Rotary Heat Exchanger | Current value | Standard | DRHX_RpmOut |  | 3x0093 | 1.00 | 0 | 3000 | Rotary heat exchanger – speed output [1/10 rpm]
Rotary Heat Exchanger | Current value | Standard | DRHX_Power_In |  | 3x0095 | 1.00 | 0 | 6000 | Rotary heat exchanger – output power [W] (only with OJ RHX2M)
Rotary Heat Exchanger | Set point | Standard | DRHX_PercentSet |  | 3x0098 | 1.00 | 0 | 10000 | Rotary heat exchanger – percentage setpoint [1/100%] (only with OJ DRHX)
AHU controller | Time | Standard | RTC_WeekDay |  | 3x0110 | 1.00 | 1 | 7 | Actual day of the week (1=Mon..7=Sun)
AHU controller | Alarm | Standard | AL_Hist_GrpNum_AlrNum+0 |  | 3x0120 | 1.00 | 0 | 25100 | Stack for active alarms (0 indicates end of stack) AlrGrp AlrNo
AHU controller | Alarm | Standard | AL_Hist_GrpNum_AlrNum+1 |  | 3x0121 | 1.00 | 0 | 25100 | Stack for active alarms (0 indicates end of stack)
AHU controller | Alarm | Standard | AL_Hist_GrpNum_AlrNum+2 |  | 3x0122 | 1.00 | 0 | 25100 | Stack for active alarms (0 indicates end of stack)
AHU controller | Alarm | Standard | AL_Hist_GrpNum_AlrNum+3 |  | 3x0123 | 1.00 | 0 | 25100 | Stack for active alarms (0 indicates end of stack)
AHU controller | Alarm | Standard | AL_Hist_GrpNum_AlrNum+4 |  | 3x0124 | 1.00 | 0 | 25100 | Stack for active alarms (0 indicates end of stack)
AHU controller | Alarm | Standard | AL_Hist_GrpNum_AlrNum+5 |  | 3x0125 | 1.00 | 0 | 25100 | Stack for active alarms (0 indicates end of stack)
AHU controller | Alarm | Standard | AL_Hist_GrpNum_AlrNum+6 |  | 3x0126 | 1.00 | 0 | 25100 | Stack for active alarms (0 indicates end of stack)
AHU controller | Alarm | Standard | AL_Hist_GrpNum_AlrNum+7 |  | 3x0127 | 1.00 | 0 | 25100 | Stack for active alarms (0 indicates end of stack)
AHU controller | Alarm | Standard | AL_Hist_GrpNum_AlrNum+8 |  | 3x0128 | 1.00 | 0 | 25100 | Stack for active alarms (0 indicates end of stack)
AHU controller | Alarm | Standard | AL_Hist_GrpNum_AlrNum+9 |  | 3x0129 | 1.00 | 0 | 25100 | Stack for active alarms (0 indicates end of stack)
AHU controller | Alarm | Standard | AL_Hist_GrpNum_AlrNum+10 |  | 3x0130 | 1.00 | 0 | 25100 | Stack for active alarms (0 indicates end of stack)
AHU controller | Alarm | Standard | AL_Hist_GrpNum_AlrNum+11 |  | 3x0131 | 1.00 | 0 | 25100 | Stack for active alarms (0 indicates end of stack)
AHU controller | Alarm | Standard | AL_Hist_GrpNum_AlrNum+12 |  | 3x0132 | 1.00 | 0 | 25100 | Stack for active alarms (0 indicates end of stack)
AHU controller | Alarm | Standard | AL_Hist_GrpNum_AlrNum+13 |  | 3x0133 | 1.00 | 0 | 25100 | Stack for active alarms (0 indicates end of stack)
AHU controller | Alarm | Standard | AL_Hist_GrpNum_AlrNum+14 |  | 3x0134 | 1.00 | 0 | 25100 | Stack for active alarms (0 indicates end of stack)
AHU controller | Alarm | Standard | AL_Hist_GrpNum_AlrNum+15 |  | 3x0135 | 1.00 | 0 | 25100 | Stack for active alarms (0 indicates end of stack)
AHU controller | SW version | Standard | SoftwareVersion |  | 3x0140 | 1.00 | 100 | 999 | Master software version [1/100]
AHU controller | SW version | Standard | SoftwareBetaVersion |  | 3x0141 | 1.00 | 0 | 999 | Master software Betaversion [1/100]
AHU controller | SW version | Standard | BootLoaderVersion |  | 3x0142 | 1.00 | 100 | 999 | Bootloader software version [1/100]
Filter, Outdoor |  | Standard | FM_SF_OA_FM_Type_UserSet |  | 3x160 | 1.00 | 0 | 3 | 0-not filter, 1-Timer, 2-Static, 3-dynamic, 4-Switch
Filter, Outdoor | Current value | Standard | FM_SF_OA_Status |  | 3x161 | 1.00 | 0 | 10000 | Outdoor filter monitor status [1/100%], ONLY IN DYNAMIC MODE FM_SF_OA_FM_Type_UserSet==3
Filter, Outdoor | Current value | Standard | FM_SF_OA_Timer_Rest_h |  | 3x162 | 1.00 | 0 | 8800 | Hours until timer alarm from the outdoor filter, FM_SF_OA_FM_Type_UserSet==1
Filter, Outdoor |  | Standard | FM_SF_OA_SwitchStatus |  | 3x163 | 1.00 | 0 | 1 | FM OA Filterswitch state, FM_SF_OA_FM_Type_UserSet==4
Filter, Extract |  | Standard | FM_SF_EA_FM_Type_UserSet |  | 3x164 | 1.00 | 0 | 3 | 0-not filter, 1-Timer, 2-Static, 3-dynamic, 4-Switch
Filter, Extract | Current value | Standard | FM_SF_EA_Status |  | 3x165 | 1.00 | 0 | 10000 | Extract filter monitor status [1/100%], ONLY IN DYNAMIC MODE FM_SF_EA_FM_Type_UserSet==3
Filter, Extract | Current value | Standard | FM_SF_EA_Timer_Rest_h |  | 3x166 | 1.00 | 0 | 8800 | Hours until timer alarm from the outdoor filter, FM_SF_EA_FM_Type_UserSet==1
Filter, Extract |  | Standard | FM_SF_EA_SwitchStatus |  | 3x167 | 1.00 | 0 | 1 | FM EA Filterswitch state, FM_SF_EA_FM_Type_UserSet==4
Humidity, Extract | Current value | Standard | IOC_HUMI_EA_Read |  | 3x171 | 1.00 | 0 | 10000 | Actual % rel. Humidity Extract duct [1/100 %]
|  |  | FM_SF_SA_FM_Type_UserSet |  | 3x173
|  |  | FM_SF_SA_Status | [5 empty] | Supply filter monitor status [1/100%], ONLY IN DYNAMIC MODE FM_SF_SA_FM_Type_UserSet==3
FM_SF_SA_Timer_Rest_h
FM_SF_SA_SwitchStatus
1. Info | 1. Info | 1. Info | 1. Info |  | Holding register (R/W) |  | 1. Info | 1. Info | 1. Info
AHU controller | Set point | Standard | OL_ManualUserSet |  | 4x0001 | 1.00 | 0 | 5 | 0=Not active 1=Manual stop (1) 2=Manual low 3=Manual medium 4 =Manual high 5=extended Stop (2)
AHU controller | Reg-Mode | Standard | AHU_SA_FanRegModeUserSet |  | 4x0002 | 1.00 | 0 | 7 | SA_FanRegMode 0 - Not mounted 1 - Flow 2 - Duct 3 - Demand (ppm) 4 - Fix Fan Speed 5 - Greenzone 6 - Slave 7 - Demand %rH
AHU controller | Reg-Mode | Standard | AHU_EA_FanRegModeUserSet |  | 4x0003 | 1.00 | 0 | 7 | EA_FanRegMode 0 - Not mounted 1 - Flow 2 - Duct 3 - Demand (ppm) 4 - Fix Fan Speed 5 - Greenzone 6 - Slave 7 - Demand %rH
AHU controller | Set point | Standard | PR_SA_LS_UserSet |  | 4x0004 | 1.00 | 200 | PR_SA_MED_UserSet | Setpoint for duct pressure, low supply [1/10Pa]
AHU controller | Set point | Standard | PR_SA_MED_UserSet |  | 4x0005 | 1.00 | PR_SA_LS_UserSet | PR_SA_HS_UserSet | Setpoint supply air duct pressure medium speed [1/10Pa]
AHU controller | Set point | Standard | PR_SA_HS_UserSet |  | 4x0006 | 1.00 | PR_SA_MED_UserSet | PR_SA_MS_UserSet | Setpoint for duct pressure, high supply [1/10Pa]
AHU controller | Set point | Standard | PR_EA_LS_UserSet |  | 4x0010 | 1.00 | 200 | PR_EA_MED_UserSet | Setpoint for low duct pressure, extract [1/10Pa]
AHU controller | Set point | Standard | PR_EA_MED_UserSet |  | 4x0011 | 1.00 | PR_EA_LS_UserSet | PR_EA_HS_UserSet | Setpoint exhaust air duct pressure medium speed [1/10Pa]
AHU controller | Set point | Standard | PR_EA_HS_UserSet |  | 4x0012 | 1.00 | PR_EA_MED_UserSet | PR_EA_MS_UserSet | Setpoint for high duct pressure, extract [1/10Pa]
AHU controller | Set point | Standard | AR_SA_LS_UserSet |  | 4x0015 | 1.00 | AHU_SA_MinFlow | AR_SA_MED_UserSet | Setpoint for supply flow, low speed [l/s]
AHU controller | Set point | Standard | AR_SA_MED_UserSet |  | 4x0016 | 1.00 | AR_SA_LS_UserSet | AR_SA_HS_UserSet | Setpoint supply air flow - medium speed [l/s]
AHU controller | Set point | Standard | AR_SA_HS_UserSet |  | 4x0017 | 1.00 | AR_SA_MED_UserSet | AR_SA_MS_UserSet | Setpoint for supply flow, high speed [l/s]
AHU controller | Set point | Standard | AR_EA_LS_UserSet |  | 4x0019 | 1.00 | AHU_EA_MinFlow | AR_EA_MED_UserSet | Setpoint for extract flow, low speed [l/s]
AHU controller | Set point | Standard | AR_EA_MED_UserSet |  | 4x0020 | 1.00 | AR_EA_LS_UserSet | AR_EA_HS_UserSet | Setpoint exhaust air flow - medium speed [l/s]
AHU controller | Set point | Standard | AR_EA_HS_UserSet |  | 4x0021 | 1.00 | AR_EA_MED_UserSet | AR_EA_MS_UserSet | Setpoint for extract flow, high speed [l/s]
AHU controller | Set point | Standard | FX_SA_LS_UserSet |  | 4x0023 | 1.00 | FX_SA_Min_Prc_UserSet | FX_SA_MED_UserSet | Supply Motor Lowspeed [1/100%], Fixed Fan Speed
Fan, Supply | Set point | Standard | FX_SA_MED_UserSet |  | 4x0024 | 1.00 | FX_SA_LS_UserSet | FX_SA_HS_UserSet | Supply Motor Mediumspeed [1/100%], Fixed Fan Speed
Fan, Supply | Set point | Standard | FX_SA_HS_UserSet |  | 4x0025 | 1.00 | FX_SA_MED_UserSet | FX_SA_Max_Prc_UserSet | Supply Motor Highspeed [1/100%], Fixed Fan Speed
Fan, Exhaust | Set point | Standard | FX_EA_LS_UserSet |  | 4x0028 | 1.00 | FX_EA_Min_Prc_UserSet | FX_EA_MED_UserSet | Exhaust Motor Lowspeed [1/100%], Fixed Fan Speed
Fan, Exhaust | Set point | Standard | FX_EA_MED_UserSet |  | 4x0029 | 1.00 | FX_EA_LS_UserSet | FX_EA_HS_UserSet | Exhaust Motor Mediumspeed [1/100%], Fixed Fan Speed
Fan, Exhaust | Set point | Standard | FX_EA_HS_UserSet |  | 4x0030 | 1.00 | FX_EA_MED_UserSet | FX_EA_Max_Prc_UserSet | Exhaust Motor Highspeed [1/100%], Fixed Fan Speed
AHU controller | Set point | Standard | SC_SlaveOffsetUserSet |  | 4x0033 | 1.00 | 500 | 2000 | Supply/extract motor offset, slave and CO2 control [1/100%]
AHU controller | Set point | Standard | DC_LS_CO2_UserSet |  | 4x0036 | 1.00 | 0 | 2000 | CO2 control: setpoint for low period (low CO2 value) [ppm]
AHU controller | Set point | Standard | DC_MED_CO2_UserSet |  | 4x0037 | 1.00 | 0 | 2000 | CO2 controller setpoint medium speed (med CO2 Val) [ppm]
AHU controller | Set point | Standard | DC_HS_CO2_UserSet |  | 4x0038 | 1.00 | 0 | 2000 | CO2 control: setpoint for high period (high CO2 value) [ppm]
AHU controller | Set point | Standard | VOC_LS_DemandUserSet |  | 4x0039 | 1.00 | 0 | 10000 | VOC control: setpoint for low period (low VOC value) [ppm]
AHU controller | Set point | Standard | VOC_MED_DemandUserSet |  | 4x0040 | 1.00 | 0 | 10000 | VOC controller setpoint medium speed (med VOC Val) [ppm]
AHU controller | Set point | Standard | VOC_HS_DemandUserSet |  | 4x0041 | 1.00 | 0 | 10000 | VOC control: setpoint for high period (high VOC value) [ppm]
AHU controller | Set point | Standard | DC_LS_PRH_UserSet |  | 4x0042 | 1.00 | 0 | 10000 | %rH control: setpoint for low period (low rH value) [%rH]
AHU controller | Set point | Standard | DC_MED_PRH_UserSet |  | 4x0043 | 1.00 | 0 | 10000 | %rH controller setpoint medium speed (med rH Val) [%rH]
AHU controller | Set point | Standard | DC_HS_PRH_UserSet |  | 4x0044 | 1.00 | 0 | 10000 | %rH control: setpoint for high period (high rH value) [%rH]
AHU controller | Set point | Standard | DC_SA_MinFlow_UserSet |  | 4x0045 | 1.00 | 100 | DC_SA_MaxFlow_UserSet | Demand Control SA Minflow in [1/l/s]
AHU controller | Set point | Standard | DC_SA_MaxFlow_UserSet |  | 4x0046 | 1.00 | DC_SA_MinFlow_UserSet | 30000 | Demand Control SA Maxflow in [1/l/s]
AHU controller | Set point | Standard | DC_EA_MinFlow_UserSet |  | 4x0047 | 1.00 | 100 | DC_EA_MaxFlow_UserSet | Demand Control EA Minflow in [1/l/s]
AHU controller | Set point | Standard | DC_EA_MaxFlow_UserSet |  | 4x0048 | 1.00 | DC_EA_MinFlow_UserSet | 30000 | Demand Control EA Maxflow in [1/l/s]
AHU controller | Set point | Standard | AHU_SA_GZM_Prc_Set |  | 4x0049 | 1.00 | 0 | 10000 | External signal GreenZone, supply [1/100%]
AHU controller | Set point | Standard | AHU_EA_GZM_Prc_Set |  | 4x0050 | 1.00 | 0 | 10000 | External signal GreenZone, exhaust [1/100%]
AHU controller | Set point | Standard | AR_SA_Reg_PB_UserSet |  | 4x0055 | 1.00 | 100 | 4000 | Flow-Regulator SA P-Band in [1/100%]
AHU controller | Set point | Standard | AR_SA_Reg_It_UserSet |  | 4x0056 | 1.00 | 1 | 1800 | Flow SA I-Time in [1/1sec]
AHU controller | Set point | Standard | AR_EA_Reg_PB_UserSet |  | 4x0057 | 1.00 | 100 | 4000 | Flow EA P-Band in [1/100%]
AHU controller | Set point | Standard | AR_EA_Reg_It_UserSet |  | 4x0058 | 1.00 | 1 | 1800 | Flow EA I-Time in [1/1sec]
AHU controller | Set point | Standard | PR_SA_Reg_PB_UserSet |  | 4x0059 | 1.00 | 100 | 4000 | Pressure SA P-Band in [1/100%]
AHU controller | Set point | Standard | PR_SA_Reg_It_UserSet |  | 4x0060 | 1.00 | 1 | 1800 | Pressure SA I-Time in [1/1sec]
AHU controller | Set point | Standard | PR_EA_Reg_PB_UserSet |  | 4x0061 | 1.00 | 100 | 4000 | Pressure EA P-Band in [1/100%]
AHU controller | Set point | Standard | PR_EA_Reg_It_UserSet |  | 4x0062 | 1.00 | 1 | 1800 | Pressure EA I-Time in [1/1sec]
AHU controller | Set point | Standard | DC_VOC_Reg_PB_UserSet |  | 4x0063 | 1.00 | 0 | 10000 | P-Band VOC [ppm]
AHU controller | Set point | Standard | DC_CO2_Reg_PB_UserSet |  | 4x0064 | 1.00 | 0 | 10000 | P-Band CO2 [ppm]
AHU controller | Set point | Standard | DC_Reg_It_UserSet |  | 4x0065 | 1.00 | 0 | 30000 | I-Time (VOC/CO2 [1/1sec]
AHU controller | Summer Night Cooling | Standard | SN_AR_SA_Flow_UserSet |  | 4x0066 | 1.00 | AHU_SA_MinFlow | AR_SA_MS_UserSet | Setpoint supply air volume sommernight cooling
AHU controller | Summer Night Cooling | Standard | SN_AR_EA_Flow_UserSet |  | 4x0067 | 1.00 | AHU_EA_MinFlow | AR_EA_MS_UserSet | Setpoint extract air volume sommernight cooling [m3/h]
AHU controller | Summer Night Cooling | Standard | SN_PR_SA_Press_UserSet |  | 4x0068 | 1.00 | DUCT_PRESSURE_MIN | PR_SA_Max_Set | Setpoint supply air pressure sommernight cooling [Pa]
AHU controller | Summer Night Cooling | Standard | SN_PR_EA_Press_UserSet |  | 4x0069 | 1.00 | DUCT_PRESSURE_MIN | PR_EA_Max_Set | Setpoint extract air pressure sommernight cooling [Pa]
AHU controller | Summer Night Cooling | Standard | SN_FX_SA_Prc_UserSet |  | 4x0070 | 1.00 | FX_SA_Min_Prc_UserSet | FX_SA_Max_Prc_UserSet | Setpoint supply air constant speed sommernight cooling [1/100%]
AHU controller | Summer Night Cooling | Standard | SN_FX_EA_Prc_UserSet |  | 4x0071 | 1.00 | FX_EA_Min_Prc_UserSet | FX_EA_Max_Prc_UserSet | Setpoint extract air constant speed sommernight cooling [1/100%]
AHU controller | Fire | Standard | AH_Fire1_SA_PrcUserSet |  | 4x0080 | 1.00 | 0 | 10000 | Supply motor speed setpoint in case of fire alarm [1/100%]
AHU controller | Fire | Standard | AH_Fire1_EA_PrcUserSet |  | 4x0081 | 1.00 | 0 | 10000 | Extract motor speed setpoint in case of fire alarm [1/100%]
AHU controller | Fire | Standard | AH_FireInt_SA_TempSet |  | 4x0082 | 1.00 | 5000 | 12000 | Limit for SA Temperature internal Fire [1/100°C]
AHU controller | Fire | Standard | AH_FireInt_EA_TempSet |  | 4x0083 | 1.00 | 3500 | 12000 | Limit for EA Temperature internal Fire [1/100°C]
AHU controller | Control | Standard | TR_RegType_UserSet |  | 4x0090 | 1.00 | 0 | 3 | 0=not available,1-supply, 2-Extract, 3=Room
AHU controller | Set point | Standard | TR_SA_Temp_UserSet |  | 4x0091 | 1.00 | 500 | 4000 | Temperature setpoint for Supply control type [1/100°C]
AHU controller | Set point | Standard | TR_EA_Temp_UserSet |  | 4x0092 | 1.00 | 500 | 4000 | Temperature setpoint for Extract control type [1/100°C]
AHU controller | Set point | Standard | TR_EA_SA_MinTemp_UserSet |  | 4x0093 | 1.00 | 0 | 3000 | Min. limit supply temperature [1/100°C] Extract/Room
AHU controller | Set point | Standard | TR_EA_SA_MaxTemp_UserSet |  | 4x0094 | 1.00 | 800 | 5000 | Max. limit supply temperature [1/100°C] Extract/Room
AHU controller | Set point | Standard | TR_RM_Temp_UserSet |  | 4x0095 | 1.00 | 500 | 4000 | Temperature setpoint for Room control type [1/100°C]
AHU controller | Control | Standard | TR_EA_PB_UserSet |  | 4x0100 | 1.00 | 100 | 4000 | P-band for extract air temperature control [1/100°C]
AHU controller | Control | Standard | TR_EA_It_UserSet |  | 4x0101 | 1.00 | 1 | 1800 | Heat / Cool I-Time for Extract-Regulator [1/sec]
AHU controller | Control | Standard | TR_SA_CL_RC_PB_UserSet |  | 4x0102 | 1.00 | 100 | 4000 | P-Band for supply coolsource control [1/100°C]
AHU controller | Control | Standard | TR_SA_CL_HX_PB_UserSet |  | 4x0103 | 1.00 | 100 | 4000 | P-Band for supply cool exchanger control [1/100°C]
AHU controller | Control | Standard | TR_SA_HT_HX_PB_UserSet |  | 4x0104 | 1.00 | 100 | 4000 | P-Band for supply heat exchanger control [1/100°C]
AHU controller | Control | Standard | TR_SA_HT_RH_PB_UserSet |  | 4x0105 | 1.00 | 100 | 4000 | P-Band for supply heatsource control [1/100°C]
AHU controller | Control | Standard | TR_SA_HT_DNRG_PB_UserSet |  | 4x0106 | 1.00 | 100 | 4000 | P-Band for supply heat flowdown control [1/100°C]
AHU controller | Control | Standard | TR_SA_CL_RC_It_UserSet |  | 4x0107 | 1.00 | 1 | 1800 | I-time for supply heat flowdown control [sec]
AHU controller | Control | Standard | TR_SA_CL_HX_It_UserSet |  | 4x0108 | 1.00 | 1 | 1800 | I-time for supply cool exchanger control [sec]
AHU controller | Control | Standard | TR_SA_HT_HX_It_UserSet |  | 4x0109 | 1.00 | 1 | 1800 | I-time for supply heat exchanger control [sec]
AHU controller | Control | Standard | TR_SA_HT_RH_It_UserSet |  | 4x0110 | 1.00 | 1 | 1800 | I-time for supply heatsource control [sec]
AHU controller | Control | Standard | TR_SA_HT_DNRG_It_UserSet |  | 4x0111 | 1.00 | 1 | 1800 | I-time for supply heat flowdown control [sec]
AHU controller | Set point | Standard | CL_RC_MinOA_Tmp_UserSet |  | 4x0115 | 1.00 | -3000 | 3000 | Min. outdoor temperature for start of cooling
AHU controller | Set point | Standard | OL_SU_HW_PowerUserSet |  | 4x0117 | 1.00 | 0 | 10000 | Heating coil: Startup power setpoint [1/100%]
AHU controller | Set point | Standard | HT_RH_FP_AHU_StopUserSet |  | 4x0118 | 1.00 | 0 | 4000 | Setpoint for frost protection control when unit is in STOP mode [1/100°C]
AHU controller | Set point | Standard | HT_RH_FP_AHU_RunUserSet |  | 4x0119 | 1.00 | 0 | 4000 | Setpoint for frost prot. control when unit is in OPERATING mode [1/100°C]
AHU controller | Set point | Standard | HT_RH_FP_AlrLim_UserSet |  | 4x0120 | 1.00 | 0 | 4000 | Setpoint for frost protection temp. alarm [1/100°C]
AHU controller | Time | Standard | RTC_YearUserSet |  | 4x0130 | 1.00 | 2000 | 2099 | Actual year
AHU controller | Time | Standard | RTC_MonthUserSet |  | 4x0131 | 1.00 | 1 | 12 | Actual month
AHU controller | Time | Standard | RTC_DateUserSet |  | 4x0132 | 1.00 | 1 | 31 | Actual date
AHU controller | Time | Standard | RTC_HourUserSet |  | 4x0133 | 1.00 | 0 | 23 | Actual hour
AHU controller | Time | Standard | RTC_MinuteUserSet |  | 4x0134 | 1.00 | 0 | 59 | Actual minutes
AHU controller | Time | Standard | RTC_SecondUserSet |  | 4x0135 | 1.00 | 0 | 59 | Actual seconds
AHU controller | Summer Night Cooling | Standard | SN_RM_StartTmpUserSet |  | 4x0140 | 1.00 | 0 | 4000 | Summer night extract/room temp. start [1/100°C]
AHU controller | Summer Night Cooling | Standard | SN_RM_StopTmpUserSet |  | 4x0141 | 1.00 | 0 | 4000 | Summer night extract/room temp. stop [1/100°C]
AHU controller | Summer Night Cooling | Standard | SN_OA_StopTmpUserSet |  | 4x0142 | 1.00 | 0 | 4000 | Summer night outdoor temp. start [1/100°C]
AHU controller | Summer Night Cooling | Standard | SN_MinSA_TempUserSet |  | 4x0143 | 1.00 | 0 | 4000 | Summer night supply temp. control setpoint [1/100°C]
AHU controller | Summer Night Cooling | Standard | SN_StartHourUserSet |  | 4x0144 | 1.00 | 0 | 23 | Summer night start [h]
AHU controller | Summer Night Cooling | Standard | SN_StartMinuteUserSet |  | 4x0145 | 1.00 | 0 | 59 | Summer night start [min]
AHU controller | Summer Night Cooling | Standard | SN_StopHourUserSet |  | 4x0146 | 1.00 | 0 | 23 | Summer night stop [h]
AHU controller | Summer Night Cooling | Standard | SN_StopMinuteUserSet |  | 4x0147 | 1.00 | 0 | 59 | Summer night stop [min]
AHU controller | Alarm | Standard | AH_SA_TempDiffAlrLimit |  | 4x0148 | 1.00 | 0 | 10000 | Alarm limit for temperature differential between supply setpoint and actual value [1/100°C]
Schedular
1. Info | 1. Info | 1. Info | 1. Info |  | Input register (R) |  | 1. Info | 1. Info | 1. Info
AHU controller | Scheduler | Standard | SO_EP_PresentValue |  | 3x0500 | 2.10 | 0 | 1
AHU controller | Scheduler | Standard | SO_ES_PresentValue_1 |  | 3x0501 | 2.10 | 0 | 1
AHU controller | Scheduler | Standard | SO_ES_PresentValue_2 |  | 3x0502 | 2.10 | 0 | 1
AHU controller | Scheduler | Standard | SO_ES_PresentValue_3 |  | 3x0503 | 2.10 | 0 | 1
AHU controller | Scheduler | Standard | SO_PresentValue |  | 3x0504 | 2.10 | 0 | 5
AHU controller | Scheduler | Standard | CO_PresentValue_1 |  | 3x0505 | 2.10 | 0 | 1
AHU controller | Scheduler | Standard | CO_PresentValue_2 |  | 3x0506 | 2.10 | 0 | 1
AHU controller | Scheduler | Standard | CO_PresentValue_3 |  | 3x0507 | 2.10 | 0 | 1
1. Info | 1. Info | 1. Info | 1. Info |  | Holding register (R/W) |  | 1. Info | 1. Info | 1. Info
AHU controller | Scheduler | Standard | SO_EP_AlwaysON |  | 4x0500 | 2.10 | 0 | 1
AHU controller | Scheduler | Standard | SO_EP_StartYear |  | 4x0501 | 2.10 | 2000 | 2099 | Properties, Schedule start year
AHU controller | Scheduler | Standard | SO_EP_StartMonth |  | 4x0502 | 2.10 | 0 | 14 | 0-Unspecified, 13-odd month, 14-even month (Properties schedule start month)
AHU controller | Scheduler | Standard | SO_EP_StartDate |  | 4x0503 | 2.10 | 0 | 34 | 0-Unspecified, 32-Last day, 33-odd, 34-even day (Properties schedule start date)
AHU controller | Scheduler | Standard | SO_EP_StartWeekday |  | 4x0504 | 2.10 | 0 | 7 | 0-Unspecified, 1..7 = Monday..Sunday
AHU controller | Scheduler | Standard | SO_EP_StopYear |  | 4x0505 | 2.10 | 2000 | 2099 | Properties, Schedule stop year
AHU controller | Scheduler | Standard | SO_EP_StopMonth |  | 4x0506 | 2.10 | 0 | 14 | 0-Unspecified, 13-odd month, 14-even month (Properties schedule stop month)
AHU controller | Scheduler | Standard | SO_EP_StopDate |  | 4x0507 | 2.10 | 0 | 34 | 0-Unspecified, 32-Last day, 33-odd, 34-even day (Properties schedule stop date)
AHU controller | Scheduler | Standard | SO_EP_StopWeekday |  | 4x0508 | 2.10 | 0 | 7 | 0-Unspecified, 1..7 = Monday..Sunday
AHU controller | Scheduler | Standard | SO_WS_MondayHour Event1 |  | 4x0509 | 2.10 | 0 | 23 | Monday, 1. event hour
AHU controller | Scheduler | Standard | SO_WS_MondayHour Event2 |  | 4x0510 | 2.10 | 0 | 23 | Monday, 2. event hour
AHU controller | Scheduler | Standard | SO_WS_MondayHour Event3 |  | 4x0511 | 2.10 | 0 | 23 | Monday, 3. event hour
AHU controller | Scheduler | Standard | SO_WS_MondayHour Event4 |  | 4x0512 | 2.10 | 0 | 23 | Monday, 4. event hour
AHU controller | Scheduler | Standard | SO_WS_MondayHour Event5 |  | 4x0513 | 2.10 | 0 | 23 | Monday, 5. event hour
AHU controller | Scheduler | Standard | SO_WS_MondayHour Event6 |  | 4x0514 | 2.10 | 0 | 23 | Monday, 6. event hour
AHU controller | Scheduler | Standard | SO_WS_MondayMinute Event1 |  | 4x0515 | 2.10 | 0 | 59 | Monday, 1. event Minute
AHU controller | Scheduler | Standard | SO_WS_MondayMinute Event2 |  | 4x0516 | 2.10 | 0 | 59 | Monday, 2. event Minute
AHU controller | Scheduler | Standard | SO_WS_MondayMinute Event3 |  | 4x0517 | 2.10 | 0 | 59 | Monday, 3. event Minute
AHU controller | Scheduler | Standard | SO_WS_MondayMinute Event4 |  | 4x0518 | 2.10 | 0 | 59 | Monday, 4. event Minute
AHU controller | Scheduler | Standard | SO_WS_MondayMinute Event5 |  | 4x0519 | 2.10 | 0 | 59 | Monday, 5. event Minute
AHU controller | Scheduler | Standard | SO_WS_MondayMinute Event6 |  | 4x0520 | 2.10 | 0 | 59 | Monday, 6. event Minute
AHU controller | Scheduler | Standard | SO_WS_MondayValue Event1 |  | 4x0521 | 2.10 | 0 | 6 | Monday, 1. event, 0-Off, 6-Fallback , 1-Stop, 2-Low, 3-Med, 4-High, 5-Extended stop
AHU controller | Scheduler | Standard | SO_WS_MondayValue Event2 |  | 4x0522 | 2.10 | 0 | 6 | Monday, 2. event, 0-Off, 6-Fallback , 1-Stop, 2-Low, 3-Med, 4-High, 5-Extended stop
AHU controller | Scheduler | Standard | SO_WS_MondayValue Event3 |  | 4x0523 | 2.10 | 0 | 6 | Monday, 3. event, 0-Off, 6-Fallback , 1-Stop, 2-Low, 3-Med, 4-High, 5-Extended stop
AHU controller | Scheduler | Standard | SO_WS_MondayValue Event4 |  | 4x0524 | 2.10 | 0 | 6 | Monday, 4. event, 0-Off, 6-Fallback , 1-Stop, 2-Low, 3-Med, 4-High, 5-Extended stop
AHU controller | Scheduler | Standard | SO_WS_MondayValue Event5 |  | 4x0525 | 2.10 | 0 | 6 | Monday, 5. event, 0-Off, 6-Fallback , 1-Stop, 2-Low, 3-Med, 4-High, 5-Extended stop
AHU controller | Scheduler | Standard | SO_WS_MondayValue Event6 |  | 4x0526 | 2.10 | 0 | 6 | Monday, 6. event, 0-Off, 6-Fallback , 1-Stop, 2-Low, 3-Med, 4-High, 5-Extended stop
AHU controller | Scheduler | Standard | SO_WS_TuesdayHour Event1 |  | 4x0527 | 2.10 | 0 | 23 | Tuesday, 1. event hour
AHU controller | Scheduler | Standard | SO_WS_TuesdayHour Event2 |  | 4x0528 | 2.10 | 0 | 23 | Tuesday, 2. event hour
AHU controller | Scheduler | Standard | SO_WS_TuesdayHour Event3 |  | 4x0529 | 2.10 | 0 | 23 | Tuesday, 3. event hour
AHU controller | Scheduler | Standard | SO_WS_TuesdayHour Event4 |  | 4x0530 | 2.10 | 0 | 23 | Tuesday, 4. event hour
AHU controller | Scheduler | Standard | SO_WS_TuesdayHour Event5 |  | 4x0531 | 2.10 | 0 | 23 | Tuesday, 5. event hour
AHU controller | Scheduler | Standard | SO_WS_TuesdayHour Event6 |  | 4x0532 | 2.10 | 0 | 23 | Tuesday, 6. event hour
AHU controller | Scheduler | Standard | SO_WS_TuesdayMinute Event1 |  | 4x0533 | 2.10 | 0 | 59 | Tuesday, 1. event Minute
AHU controller | Scheduler | Standard | SO_WS_TuesdayMinute Event2 |  | 4x0534 | 2.10 | 0 | 59 | Tuesday, 2. event Minute
AHU controller | Scheduler | Standard | SO_WS_TuesdayMinute Event3 |  | 4x0535 | 2.10 | 0 | 59 | Tuesday, 3. event Minute
AHU controller | Scheduler | Standard | SO_WS_TuesdayMinute Event4 |  | 4x0536 | 2.10 | 0 | 59 | Tuesday, 4. event Minute
AHU controller | Scheduler | Standard | SO_WS_TuesdayMinute Event5 |  | 4x0537 | 2.10 | 0 | 59 | Tuesday, 5. event Minute
AHU controller | Scheduler | Standard | SO_WS_TuesdayMinute Event6 |  | 4x0538 | 2.10 | 0 | 59 | Tuesday, 6. event Minute
AHU controller | Scheduler | Standard | SO_WS_TuesdayValue Event1 |  | 4x0539 | 2.10 | 0 | 6 | Tuesday, 1. event, 0-Off, 6-Fallback , 1-Stop, 2-Low, 3-Med, 4-High, 5-Extended stop
AHU controller | Scheduler | Standard | SO_WS_TuesdayValue Event2 |  | 4x0540 | 2.10 | 0 | 6 | Tuesday, 2. event, 0-Off, 6-Fallback , 1-Stop, 2-Low, 3-Med, 4-High, 5-Extended stop
AHU controller | Scheduler | Standard | SO_WS_TuesdayValue Event3 |  | 4x0541 | 2.10 | 0 | 6 | Tuesday, 3. event, 0-Off, 6-Fallback , 1-Stop, 2-Low, 3-Med, 4-High, 5-Extended stop
AHU controller | Scheduler | Standard | SO_WS_TuesdayValue Event4 |  | 4x0542 | 2.10 | 0 | 6 | Tuesday, 4. event, 0-Off, 6-Fallback , 1-Stop, 2-Low, 3-Med, 4-High, 5-Extended stop
AHU controller | Scheduler | Standard | SO_WS_TuesdayValue Event5 |  | 4x0543 | 2.10 | 0 | 6 | Tuesday, 5. event, 0-Off, 6-Fallback , 1-Stop, 2-Low, 3-Med, 4-High, 5-Extended stop
AHU controller | Scheduler | Standard | SO_WS_TuesdayValue Event6 |  | 4x0544 | 2.10 | 0 | 6 | Tuesday, 6. event, 0-Off, 6-Fallback , 1-Stop, 2-Low, 3-Med, 4-High, 5-Extended stop
AHU controller | Scheduler | Standard | SO_WS_WednesdayHour Event1 |  | 4x0545 | 2.10 | 0 | 23 | Wednesday, 1. event hour
AHU controller | Scheduler | Standard | SO_WS_WednesdayHour Event2 |  | 4x0546 | 2.10 | 0 | 23 | Wednesday, 2. event hour
AHU controller | Scheduler | Standard | SO_WS_WednesdayHour Event3 |  | 4x0547 | 2.10 | 0 | 23 | Wednesday, 3. event hour
AHU controller | Scheduler | Standard | SO_WS_WednesdayHour Event4 |  | 4x0548 | 2.10 | 0 | 23 | Wednesday, 4. event hour
AHU controller | Scheduler | Standard | SO_WS_WednesdayHour Event5 |  | 4x0549 | 2.10 | 0 | 23 | Wednesday, 5. event hour
AHU controller | Scheduler | Standard | SO_WS_WednesdayHour Event6 |  | 4x0550 | 2.10 | 0 | 23 | Wednesday, 6. event hour
AHU controller | Scheduler | Standard | SO_WS_WednesdayMinute Event1 |  | 4x0551 | 2.10 | 0 | 59 | Wednesday, 1. event Minute
AHU controller | Scheduler | Standard | SO_WS_WednesdayMinute Event2 |  | 4x0552 | 2.10 | 0 | 59 | Wednesday, 2. event Minute
AHU controller | Scheduler | Standard | SO_WS_WednesdayMinute Event3 |  | 4x0553 | 2.10 | 0 | 59 | Wednesday, 3. event Minute
AHU controller | Scheduler | Standard | SO_WS_WednesdayMinute Event4 |  | 4x0554 | 2.10 | 0 | 59 | Wednesday, 4. event Minute
AHU controller | Scheduler | Standard | SO_WS_WednesdayMinute Event5 |  | 4x0555 | 2.10 | 0 | 59 | Wednesday, 5. event Minute
AHU controller | Scheduler | Standard | SO_WS_WednesdayMinute Event6 |  | 4x0556 | 2.10 | 0 | 59 | Wednesday, 6. event Minute
AHU controller | Scheduler | Standard | SO_WS_WednesdayValue Event1 |  | 4x0557 | 2.10 | 0 | 6 | Wednesday, 1. event, 0-Off, 6-Fallback , 1-Stop, 2-Low, 3-Med, 4-High, 5-Extended stop
AHU controller | Scheduler | Standard | SO_WS_WednesdayValue Event2 |  | 4x0558 | 2.10 | 0 | 6 | Wednesday, 2. event, 0-Off, 6-Fallback , 1-Stop, 2-Low, 3-Med, 4-High, 5-Extended stop
AHU controller | Scheduler | Standard | SO_WS_WednesdayValue Event3 |  | 4x0559 | 2.10 | 0 | 6 | Wednesday, 3. event, 0-Off, 6-Fallback , 1-Stop, 2-Low, 3-Med, 4-High, 5-Extended stop
AHU controller | Scheduler | Standard | SO_WS_WednesdayValue Event4 |  | 4x0560 | 2.10 | 0 | 6 | Wednesday, 4. event, 0-Off, 6-Fallback , 1-Stop, 2-Low, 3-Med, 4-High, 5-Extended stop
AHU controller | Scheduler | Standard | SO_WS_WednesdayValue Event5 |  | 4x0561 | 2.10 | 0 | 6 | Wednesday, 5. event, 0-Off, 6-Fallback , 1-Stop, 2-Low, 3-Med, 4-High, 5-Extended stop
AHU controller | Scheduler | Standard | SO_WS_WednesdayValue Event6 |  | 4x0562 | 2.10 | 0 | 6 | Wednesday, 6. event, 0-Off, 6-Fallback , 1-Stop, 2-Low, 3-Med, 4-High, 5-Extended stop
AHU controller | Scheduler | Standard | SO_WS_ThursdayHour Event1 |  | 4x0563 | 2.10 | 0 | 23 | Thursday, 1. event hour
AHU controller | Scheduler | Standard | SO_WS_ThursdayHour Event2 |  | 4x0564 | 2.10 | 0 | 23 | Thursday, 2. event hour
AHU controller | Scheduler | Standard | SO_WS_ThursdayHour Event3 |  | 4x0565 | 2.10 | 0 | 23 | Thursday, 3. event hour
AHU controller | Scheduler | Standard | SO_WS_ThursdayHour Event4 |  | 4x0566 | 2.10 | 0 | 23 | Thursday, 4. event hour
AHU controller | Scheduler | Standard | SO_WS_ThursdayHour Event5 |  | 4x0567 | 2.10 | 0 | 23 | Thursday, 5. event hour
AHU controller | Scheduler | Standard | SO_WS_ThursdayHour Event6 |  | 4x0568 | 2.10 | 0 | 23 | Thursday, 6. event hour
AHU controller | Scheduler | Standard | SO_WS_ThursdayMinute Event1 |  | 4x0569 | 2.10 | 0 | 59 | Thursday, 1. event Minute
AHU controller | Scheduler | Standard | SO_WS_ThursdayMinute Event2 |  | 4x0570 | 2.10 | 0 | 59 | Thursday, 2. event Minute
AHU controller | Scheduler | Standard | SO_WS_ThursdayMinute Event3 |  | 4x0571 | 2.10 | 0 | 59 | Thursday, 3. event Minute
AHU controller | Scheduler | Standard | SO_WS_ThursdayMinute Event4 |  | 4x0572 | 2.10 | 0 | 59 | Thursday, 4. event Minute
AHU controller | Scheduler | Standard | SO_WS_ThursdayMinute Event5 |  | 4x0573 | 2.10 | 0 | 59 | Thursday, 5. event Minute
AHU controller | Scheduler | Standard | SO_WS_ThursdayMinute Event6 |  | 4x0574 | 2.10 | 0 | 59 | Thursday, 6. event Minute
AHU controller | Scheduler | Standard | SO_WS_ThursdayValue Event1 |  | 4x0575 | 2.10 | 0 | 6 | Thursday, 1. event, 0-Off, 6-Fallback , 1-Stop, 2-Low, 3-Med, 4-High, 5-Extended stop
AHU controller | Scheduler | Standard | SO_WS_ThursdayValue Event2 |  | 4x0576 | 2.10 | 0 | 6 | Thursday, 2. event, 0-Off, 6-Fallback , 1-Stop, 2-Low, 3-Med, 4-High, 5-Extended stop
AHU controller | Scheduler | Standard | SO_WS_ThursdayValue Event3 |  | 4x0577 | 2.10 | 0 | 6 | Thursday, 3. event, 0-Off, 6-Fallback , 1-Stop, 2-Low, 3-Med, 4-High, 5-Extended stop
AHU controller | Scheduler | Standard | SO_WS_ThursdayValue Event4 |  | 4x0578 | 2.10 | 0 | 6 | Thursday, 4. event, 0-Off, 6-Fallback , 1-Stop, 2-Low, 3-Med, 4-High, 5-Extended stop
AHU controller | Scheduler | Standard | SO_WS_ThursdayValue Event5 |  | 4x0579 | 2.10 | 0 | 6 | Thursday, 5. event, 0-Off, 6-Fallback , 1-Stop, 2-Low, 3-Med, 4-High, 5-Extended stop
AHU controller | Scheduler | Standard | SO_WS_ThursdayValue Event6 |  | 4x0580 | 2.10 | 0 | 6 | Thursday, 6. event, 0-Off, 6-Fallback , 1-Stop, 2-Low, 3-Med, 4-High, 5-Extended stop
AHU controller | Scheduler | Standard | SO_WS_FridayHour Event1 |  | 4x0581 | 2.10 | 0 | 23 | Friday, 1. event hour
AHU controller | Scheduler | Standard | SO_WS_FridayHour Event2 |  | 4x0582 | 2.10 | 0 | 23 | Friday, 2. event hour
AHU controller | Scheduler | Standard | SO_WS_FridayHour Event3 |  | 4x0583 | 2.10 | 0 | 23 | Friday, 3. event hour
AHU controller | Scheduler | Standard | SO_WS_FridayHour Event4 |  | 4x0584 | 2.10 | 0 | 23 | Friday, 4. event hour
AHU controller | Scheduler | Standard | SO_WS_FridayHour Event5 |  | 4x0585 | 2.10 | 0 | 23 | Friday, 5. event hour
AHU controller | Scheduler | Standard | SO_WS_FridayHour Event6 |  | 4x0586 | 2.10 | 0 | 23 | Friday, 6. event hour
AHU controller | Scheduler | Standard | SO_WS_FridayMinute Event1 |  | 4x0587 | 2.10 | 0 | 59 | Friday, 1. event Minute
AHU controller | Scheduler | Standard | SO_WS_FridayMinute Event2 |  | 4x0588 | 2.10 | 0 | 59 | Friday, 2. event Minute
AHU controller | Scheduler | Standard | SO_WS_FridayMinute Event3 |  | 4x0589 | 2.10 | 0 | 59 | Friday, 3. event Minute
AHU controller | Scheduler | Standard | SO_WS_FridayMinute Event4 |  | 4x0590 | 2.10 | 0 | 59 | Friday, 4. event Minute
AHU controller | Scheduler | Standard | SO_WS_FridayMinute Event5 |  | 4x0591 | 2.10 | 0 | 59 | Friday, 5. event Minute
AHU controller | Scheduler | Standard | SO_WS_FridayMinute Event6 |  | 4x0592 | 2.10 | 0 | 59 | Friday, 6. event Minute
AHU controller | Scheduler | Standard | SO_WS_FridayValue Event1 |  | 4x0593 | 2.10 | 0 | 6 | Friday, 1. event, 0-Off, 6-Fallback , 1-Stop, 2-Low, 3-Med, 4-High, 5-Extended stop
AHU controller | Scheduler | Standard | SO_WS_FridayValue Event2 |  | 4x0594 | 2.10 | 0 | 6 | Friday, 2. event, 0-Off, 6-Fallback , 1-Stop, 2-Low, 3-Med, 4-High, 5-Extended stop
AHU controller | Scheduler | Standard | SO_WS_FridayValue Event3 |  | 4x0595 | 2.10 | 0 | 6 | Friday, 3. event, 0-Off, 6-Fallback , 1-Stop, 2-Low, 3-Med, 4-High, 5-Extended stop
AHU controller | Scheduler | Standard | SO_WS_FridayValue Event4 |  | 4x0596 | 2.10 | 0 | 6 | Friday, 4. event, 0-Off, 6-Fallback , 1-Stop, 2-Low, 3-Med, 4-High, 5-Extended stop
AHU controller | Scheduler | Standard | SO_WS_FridayValue Event5 |  | 4x0597 | 2.10 | 0 | 6 | Friday, 5. event, 0-Off, 6-Fallback , 1-Stop, 2-Low, 3-Med, 4-High, 5-Extended stop
AHU controller | Scheduler | Standard | SO_WS_FridayValue Event6 |  | 4x0598 | 2.10 | 0 | 6 | Friday, 6. event, 0-Off, 6-Fallback , 1-Stop, 2-Low, 3-Med, 4-High, 5-Extended stop
AHU controller | Scheduler | Standard | SO_WS_SaturdayHour Event1 |  | 4x0599 | 2.10 | 0 | 23 | Saturday, 1. event hour
AHU controller | Scheduler | Standard | SO_WS_SaturdayHour Event2 |  | 4x0600 | 2.10 | 0 | 23 | Saturday, 2. event hour
AHU controller | Scheduler | Standard | SO_WS_SaturdayHour Event3 |  | 4x0601 | 2.10 | 0 | 23 | Saturday, 3. event hour
AHU controller | Scheduler | Standard | SO_WS_SaturdayHour Event4 |  | 4x0602 | 2.10 | 0 | 23 | Saturday, 4. event hour
AHU controller | Scheduler | Standard | SO_WS_SaturdayHour Event5 |  | 4x0603 | 2.10 | 0 | 23 | Saturday, 5. event hour
AHU controller | Scheduler | Standard | SO_WS_SaturdayHour Event6 |  | 4x0604 | 2.10 | 0 | 23 | Saturday, 6. event hour
AHU controller | Scheduler | Standard | SO_WS_SaturdayMinute Event1 |  | 4x0605 | 2.10 | 0 | 59 | Saturday, 1. event Minute
AHU controller | Scheduler | Standard | SO_WS_SaturdayMinute Event2 |  | 4x0606 | 2.10 | 0 | 59 | Saturday, 2. event Minute
AHU controller | Scheduler | Standard | SO_WS_SaturdayMinute Event3 |  | 4x0607 | 2.10 | 0 | 59 | Saturday, 3. event Minute
AHU controller | Scheduler | Standard | SO_WS_SaturdayMinute Event4 |  | 4x0608 | 2.10 | 0 | 59 | Saturday, 4. event Minute
AHU controller | Scheduler | Standard | SO_WS_SaturdayMinute Event5 |  | 4x0609 | 2.10 | 0 | 59 | Saturday, 5. event Minute
AHU controller | Scheduler | Standard | SO_WS_SaturdayMinute Event6 |  | 4x0610 | 2.10 | 0 | 59 | Saturday, 6. event Minute
AHU controller | Scheduler | Standard | SO_WS_SaturdayValue Event1 |  | 4x0611 | 2.10 | 0 | 6 | Saturday, 1. event, 0-Off, 6-Fallback , 1-Stop, 2-Low, 3-Med, 4-High, 5-Extended stop
AHU controller | Scheduler | Standard | SO_WS_SaturdayValue Event2 |  | 4x0612 | 2.10 | 0 | 6 | Saturday, 2. event, 0-Off, 6-Fallback , 1-Stop, 2-Low, 3-Med, 4-High, 5-Extended stop
AHU controller | Scheduler | Standard | SO_WS_SaturdayValue Event3 |  | 4x0613 | 2.10 | 0 | 6 | Saturiday, 3. event, 0-Off, 6-Fallback , 1-Stop, 2-Low, 3-Med, 4-High, 5-Extended stop
AHU controller | Scheduler | Standard | SO_WS_SaturdayValue Event4 |  | 4x0614 | 2.10 | 0 | 6 | Saturday, 4. event, 0-Off, 6-Fallback , 1-Stop, 2-Low, 3-Med, 4-High, 5-Extended stop
AHU controller | Scheduler | Standard | SO_WS_SaturdayValue Event5 |  | 4x0615 | 2.10 | 0 | 6 | Saturday, 5. event, 0-Off, 6-Fallback , 1-Stop, 2-Low, 3-Med, 4-High, 5-Extended stop
AHU controller | Scheduler | Standard | SO_WS_SaturdayValue Event6 |  | 4x0616 | 2.10 | 0 | 6 | Saturday, 6. event, 0-Off, 6-Fallback , 1-Stop, 2-Low, 3-Med, 4-High, 5-Extended stop
AHU controller | Scheduler | Standard | SO_WS_SundayHour Event1 |  | 4x0617 | 2.10 | 0 | 23 | Sunday, 1. event hour
AHU controller | Scheduler | Standard | SO_WS_SundayHour Event2 |  | 4x0618 | 2.10 | 0 | 23 | Sunday, 2. event hour
AHU controller | Scheduler | Standard | SO_WS_SundayHour Event3 |  | 4x0619 | 2.10 | 0 | 23 | Sunday, 3. event hour
AHU controller | Scheduler | Standard | SO_WS_SundayHour Event4 |  | 4x0620 | 2.10 | 0 | 23 | Sunday, 4. event hour
AHU controller | Scheduler | Standard | SO_WS_SundayHour Event5 |  | 4x0621 | 2.10 | 0 | 23 | Sunday, 5. event hour
AHU controller | Scheduler | Standard | SO_WS_SundayHour Event6 |  | 4x0622 | 2.10 | 0 | 23 | Sunday, 6. event hour
AHU controller | Scheduler | Standard | SO_WS_SundayMinute Event1 |  | 4x0623 | 2.10 | 0 | 59 | Sunday, 1. event Minute
AHU controller | Scheduler | Standard | SO_WS_SundayMinute Event2 |  | 4x0624 | 2.10 | 0 | 59 | Sunday, 2. event Minute
AHU controller | Scheduler | Standard | SO_WS_SundayMinute Event3 |  | 4x0625 | 2.10 | 0 | 59 | Sunday, 3. event Minute
AHU controller | Scheduler | Standard | SO_WS_SundayMinute Event4 |  | 4x0626 | 2.10 | 0 | 59 | Sunday, 4. event Minute
AHU controller | Scheduler | Standard | SO_WS_SundayMinute Event5 |  | 4x0627 | 2.10 | 0 | 59 | Sunday, 5. event Minute
AHU controller | Scheduler | Standard | SO_WS_SundayMinute Event6 |  | 4x0628 | 2.10 | 0 | 59 | Sunday, 6. event Minute
AHU controller | Scheduler | Standard | SO_WS_SundayValue Event1 |  | 4x0629 | 2.10 | 0 | 6 | Sunday, 1. event, 0-Off, 6-Fallback , 1-Stop, 2-Low, 3-Med, 4-High, 5-Extended stop
AHU controller | Scheduler | Standard | SO_WS_SundayValue Evnet2 |  | 4x0630 | 2.10 | 0 | 6 | Sunday, 2. event, 0-Off, 6-Fallback , 1-Stop, 2-Low, 3-Med, 4-High, 5-Extended stop
AHU controller | Scheduler | Standard | SO_WS_SundayValue Event3 |  | 4x0631 | 2.10 | 0 | 6 | Sunday, 3. event, 0-Off, 6-Fallback , 1-Stop, 2-Low, 3-Med, 4-High, 5-Extended stop
AHU controller | Scheduler | Standard | SO_WS_SundayValue Event4 |  | 4x0632 | 2.10 | 0 | 6 | Sunday, 4. event, 0-Off, 6-Fallback , 1-Stop, 2-Low, 3-Med, 4-High, 5-Extended stop
AHU controller | Scheduler | Standard | SO_WS_SundayValue Event5 |  | 4x0633 | 2.10 | 0 | 6 | Sunday, 5. event, 0-Off, 6-Fallback , 1-Stop, 2-Low, 3-Med, 4-High, 5-Extended stop
AHU controller | Scheduler | Standard | SO_WS_SundayValue Event6 |  | 4x0634 | 2.10 | 0 | 6 | Sunday, 6. event, 0-Off, 6-Fallback , 1-Stop, 2-Low, 3-Med, 4-High, 5-Extended stop
AHU controller | Scheduler | Standard | SO_ES_1_StartYear |  | 4x0635 | 2.10 | 2000 | 2099
AHU controller | Scheduler | Standard | SO_ES_1_StartMonth |  | 4x0636 | 2.10 | 0 | 14 | 0-Unspecified, 13-odd month, 14-even month
AHU controller | Scheduler | Standard | SO_ES_1_StartDate |  | 4x0637 | 2.10 | 0 | SO_ES_1_MaxStartDate | 0-Unspecified -------------------Max = 34-------------- 32-Last day of month 33-odd days of month 34-even days of month -------------------Max = 6---------------- 1-days numbered 1..7 2-days numbered 8..14 3-days numbered 15..21 4-days numbered 22.28 5-days numbered 29..31 6-last 7 daus of month
AHU controller | Scheduler | Standard | SO_ES_1_StartWeekday |  | 4x0638 | 2.10 | 0 | 7 | 0-Unspecified, 1..7 = Monday..Sunday
AHU controller | Scheduler | Standard | SO_ES_1_StopYear |  | 4x0639 | 2.10 | 2000 | 2099
AHU controller | Scheduler | Standard | SO_ES_1_StopMonth |  | 4x0640 | 2.10 | 0 | 14 | 0-Unspecified, 13-odd month, 14-even month
AHU controller | Scheduler | Standard | SO_ES_1_StopDate |  | 4x0641 | 2.10 | 0 | 34 | 0-Unspecified, 32-Last day, 33-odd, 34-even day
AHU controller | Scheduler | Standard | SO_ES_1_StopWeekday |  | 4x0642 | 2.10 | 0 | 7 | 0-Unspecified, 1..7 = Monday..Sunday
AHU controller | Scheduler | Standard | SO_ES_1_Period |  | 4x0643 | 2.10 | 0 | 5 | 0-Date setting valid (MaxStartDate = 34) 1-Date range setting valid (MaxStartDate = 34) 2-Weekday setting valid (MaxStartDate = 6) 3-Calendar-1 setting valid (MaxStartDate = 34) 4-Calendar-2 setting valid (MaxStartDate = 34) 5-Inactive (MaxStartDate = unchanged)
AHU controller | Scheduler | Standard | SO_ES_1_EventPriority |  | 4x0644 | 2.10 | 1 | 16 | Lowest value = highest priority (if both exception 1 and 2 are active, and both "EventPriority" is equal, exception-1 has higthest priority)
AHU controller | Scheduler | Standard | SO_ES_1_Hour Event1 |  | 4x0645 | 2.10 | 0 | 23 | Exception 1, 1. event hour
AHU controller | Scheduler | Standard | SO_ES_1_Hour Event2 |  | 4x0646 | 2.10 | 0 | 23 | Exception 1, 2. event hour
AHU controller | Scheduler | Standard | SO_ES_1_Hour Event3 |  | 4x0647 | 2.10 | 0 | 23 | Exception 1, 3. event hour
AHU controller | Scheduler | Standard | SO_ES_1_Hour Event4 |  | 4x0648 | 2.10 | 0 | 23 | Exception 1, 4. event hour
AHU controller | Scheduler | Standard | SO_ES_1_Hour Event5 |  | 4x0649 | 2.10 | 0 | 23 | Exception 1, 5. event hour
AHU controller | Scheduler | Standard | SO_ES_1_Hour Event6 |  | 4x0650 | 2.10 | 0 | 23 | Exception 1, 6. event hour
AHU controller | Scheduler | Standard | SO_ES_1_Minute Event1 |  | 4x0651 | 2.10 | 0 | 59 | Exception 1, 1. event minute
AHU controller | Scheduler | Standard | SO_ES_1_Minute Event2 |  | 4x0652 | 2.10 | 0 | 59 | Exception 1, 2. event minute
AHU controller | Scheduler | Standard | SO_ES_1_Minute Event3 |  | 4x0653 | 2.10 | 0 | 59 | Exception 1, 3. event minute
AHU controller | Scheduler | Standard | SO_ES_1_Minute Event4 |  | 4x0654 | 2.10 | 0 | 59 | Exception 1, 4. event minute
AHU controller | Scheduler | Standard | SO_ES_1_Minute Event5 |  | 4x0655 | 2.10 | 0 | 59 | Exception 1, 5. event minute
AHU controller | Scheduler | Standard | SO_ES_1_Minute Event6 |  | 4x0656 | 2.10 | 0 | 59 | Exception 1, 6. event minute
AHU controller | Scheduler | Standard | SO_ES_1_Value Event1 |  | 4x0657 | 2.10 | 0 | 6 | Exception 1, 1. event, 0-Off, 6-Fallback , 1-Stop, 2-Low, 3-Med, 4-High, 5-Extended stop
AHU controller | Scheduler | Standard | SO_ES_1_Value Event2 |  | 4x0658 | 2.10 | 0 | 6 | Exception 1, 2. event, 0-Off, 6-Fallback , 1-Stop, 2-Low, 3-Med, 4-High, 5-Extended stop
AHU controller | Scheduler | Standard | SO_ES_1_Value Event3 |  | 4x0659 | 2.10 | 0 | 6 | Exception 1, 3. event, 0-Off, 6-Fallback , 1-Stop, 2-Low, 3-Med, 4-High, 5-Extended stop
AHU controller | Scheduler | Standard | SO_ES_1_Value Event4 |  | 4x0660 | 2.10 | 0 | 6 | Exception 1, 4. event, 0-Off, 6-Fallback , 1-Stop, 2-Low, 3-Med, 4-High, 5-Extended stop
AHU controller | Scheduler | Standard | SO_ES_1_Value Event5 |  | 4x0661 | 2.10 | 0 | 6 | Exception 1, 5. event, 0-Off, 6-Fallback , 1-Stop, 2-Low, 3-Med, 4-High, 5-Extended stop
AHU controller | Scheduler | Standard | SO_ES_1_Value Event6 |  | 4x0662 | 2.10 | 0 | 6 | Exception 1, 6. event, 0-Off, 6-Fallback , 1-Stop, 2-Low, 3-Med, 4-High, 5-Extended stop
AHU controller | Scheduler | Standard | SO_ES_2_StartYear |  | 4x0663 | 2.10 | 2000 | 2099
AHU controller | Scheduler | Standard | SO_ES_2_StartMonth |  | 4x0664 | 2.10 | 0 | 14 | 0-Unspecified, 13-odd month, 14-even month
AHU controller | Scheduler | Standard | SO_ES_2_StartDate |  | 4x0665 | 2.10 | 0 | SO_ES_1_MaxStartDate | 0-Unspecified -------------------Max = 34-------------- 32-Last day of month 33-odd days of month 34-even days of month -------------------Max = 6---------------- 1-days numbered 1..7 2-days numbered 8..14 3-days numbered 15..21 4-days numbered 22.28 5-days numbered 29..31 6-last 7 daus of month
AHU controller | Scheduler | Standard | SO_ES_2_StartWeekday |  | 4x0666 | 2.10 | 0 | 7 | 0-Unspecified, 1..7 = Monday..Sunday
AHU controller | Scheduler | Standard | SO_ES_2_StopYear |  | 4x0667 | 2.10 | 2000 | 2099
AHU controller | Scheduler | Standard | SO_ES_2_StopMonth |  | 4x0668 | 2.10 | 0 | 14 | 0-Unspecified, 13-odd month, 14-even month
AHU controller | Scheduler | Standard | SO_ES_2_StopDate |  | 4x0669 | 2.10 | 0 | 34 | 0-Unspecified, 32-Last day, 33-odd, 34-even day
AHU controller | Scheduler | Standard | SO_ES_2_StopWeekday |  | 4x0670 | 2.10 | 0 | 7 | 0-Unspecified, 1..7 = Monday..Sunday
AHU controller | Scheduler | Standard | SO_ES_2_Period |  | 4x0671 | 2.10 | 0 | 5 | 0-Date setting valid (MaxStartDate = 34) 1-Date range setting valid (MaxStartDate = 34) 2-Weekday setting valid (MaxStartDate = 6) 3-Calendar-1 setting valid (MaxStartDate = 34) 4-Calendar-2 setting valid (MaxStartDate = 34) 5-Inactive (MaxStartDate = unchanged)
AHU controller | Scheduler | Standard | SO_ES_2_EventPriority |  | 4x0672 | 2.10 | 1 | 16 | Lowest value = highest priority (if both exception 1 and 2 are active, and both "EventPriority" is equal, exception-1 has higthest priority)
AHU controller | Scheduler | Standard | SO_ES_2_Hour Event1 |  | 4x0673 | 2.10 | 0 | 23 | Exception 2, 1. event hour
AHU controller | Scheduler | Standard | SO_ES_2_Hour Event2 |  | 4x0674 | 2.10 | 0 | 23 | Exception 2, 2. event hour
AHU controller | Scheduler | Standard | SO_ES_2_Hour Event3 |  | 4x0675 | 2.10 | 0 | 23 | Exception 2, 3. event hour
AHU controller | Scheduler | Standard | SO_ES_2_Hour Event4 |  | 4x0676 | 2.10 | 0 | 23 | Exception 2, 4. event hour
AHU controller | Scheduler | Standard | SO_ES_2_Hour Event5 |  | 4x0677 | 2.10 | 0 | 23 | Exception 2, 5. event hour
AHU controller | Scheduler | Standard | SO_ES_2_Hour Event6 |  | 4x0678 | 2.10 | 0 | 23 | Exception 2, 6. event hour
AHU controller | Scheduler | Standard | SO_ES_2_Minute Event1 |  | 4x0679 | 2.10 | 0 | 59 | Exception 2, 1. event minute
AHU controller | Scheduler | Standard | SO_ES_2_Minute Event2 |  | 4x0680 | 2.10 | 0 | 59 | Exception 2, 2. event minute
AHU controller | Scheduler | Standard | SO_ES_2_Minute Event3 |  | 4x0681 | 2.10 | 0 | 59 | Exception 2, 3. event minute
AHU controller | Scheduler | Standard | SO_ES_2_Minute Event4 |  | 4x0682 | 2.10 | 0 | 59 | Exception 2, 4. event minute
AHU controller | Scheduler | Standard | SO_ES_2_Minute Event5 |  | 4x0683 | 2.10 | 0 | 59 | Exception 2, 5. event minute
AHU controller | Scheduler | Standard | SO_ES_2_Minute Event6 |  | 4x0684 | 2.10 | 0 | 59 | Exception 2, 6. event minute
AHU controller | Scheduler | Standard | SO_ES_2_Value Event1 |  | 4x0685 | 2.10 | 0 | 6 | Exception 2, 1. event, 0-Off, 6-Fallback , 1-Stop, 2-Low, 3-Med, 4-High, 5-Extended stop
AHU controller | Scheduler | Standard | SO_ES_2_Value Event2 |  | 4x0686 | 2.10 | 0 | 6 | Exception 2, 2. event, 0-Off, 6-Fallback , 1-Stop, 2-Low, 3-Med, 4-High, 5-Extended stop
AHU controller | Scheduler | Standard | SO_ES_2_Value Event3 |  | 4x0687 | 2.10 | 0 | 6 | Exception 2, 3. event, 0-Off, 6-Fallback , 1-Stop, 2-Low, 3-Med, 4-High, 5-Extended stop
AHU controller | Scheduler | Standard | SO_ES_2_Value Event4 |  | 4x0688 | 2.10 | 0 | 6 | Exception 2, 4. event, 0-Off, 6-Fallback , 1-Stop, 2-Low, 3-Med, 4-High, 5-Extended stop
AHU controller | Scheduler | Standard | SO_ES_2_Value Event5 |  | 4x0689 | 2.10 | 0 | 6 | Exception 2, 5. event, 0-Off, 6-Fallback , 1-Stop, 2-Low, 3-Med, 4-High, 5-Extended stop
AHU controller | Scheduler | Standard | SO_ES_2_Value Event6 |  | 4x0690 | 2.10 | 0 | 6 | Exception 2, 6. event, 0-Off, 6-Fallback , 1-Stop, 2-Low, 3-Med, 4-High, 5-Extended stop
AHU controller | Scheduler | Standard | SO_ES_3_StartYear |  | 4x0691 | 2.10 | 2000 | 2099
AHU controller | Scheduler | Standard | SO_ES_3_StartMonth |  | 4x0692 | 2.10 | 0 | 14 | 0-Unspecified, 13-odd month, 14-even month
AHU controller | Scheduler | Standard | SO_ES_3_StartDate |  | 4x0693 | 2.10 | 0 | SO_ES_1_MaxStartDate | 0-Unspecified -------------------Max = 34-------------- 32-Last day of month 33-odd days of month 34-even days of month -------------------Max = 6---------------- 1-days numbered 1..7 2-days numbered 8..14 3-days numbered 15..21 4-days numbered 22.28 5-days numbered 29..31 6-last 7 daus of month
AHU controller | Scheduler | Standard | SO_ES_3_StartWeekday |  | 4x0694 | 2.10 | 0 | 7 | 0-Unspecified, 1..7 = Monday..Sunday
AHU controller | Scheduler | Standard | SO_ES_3_StopYear |  | 4x0695 | 2.10 | 2000 | 2099
AHU controller | Scheduler | Standard | SO_ES_3_StopMonth |  | 4x0696 | 2.10 | 0 | 14 | 0-Unspecified, 13-odd month, 14-even month
AHU controller | Scheduler | Standard | SO_ES_3_StopDate |  | 4x0697 | 2.10 | 0 | 34 | 0-Unspecified, 32-Last day, 33-odd, 34-even day
AHU controller | Scheduler | Standard | SO_ES_3_StopWeekday |  | 4x0698 | 2.10 | 0 | 7 | 0-Unspecified, 1..7 = Monday..Sunday
AHU controller | Scheduler | Standard | SO_ES_3_Period |  | 4x0699 | 2.10 | 0 | 5 | 0-Date setting valid (MaxStartDate = 34) 1-Date range setting valid (MaxStartDate = 34) 2-Weekday setting valid (MaxStartDate = 6) 3-Calendar-1 setting valid (MaxStartDate = 34) 4-Calendar-2 setting valid (MaxStartDate = 34) 5-Inactive (MaxStartDate = unchanged)
AHU controller | Scheduler | Standard | SO_ES_3_EventPriority |  | 4x0700 | 2.10 | 1 | 16 | Lowest value = highest priority (if both exception 1 and 2 are active, and both "EventPriority" is equal, exception-1 has higthest priority)
AHU controller | Scheduler | Standard | SO_ES_3_Hour Event1 |  | 4x0701 | 2.10 | 0 | 23 | Exception 3, 1. event hour
AHU controller | Scheduler | Standard | SO_ES_3_Hour Event2 |  | 4x0702 | 2.10 | 0 | 23 | Exception 3, 2. event hour
AHU controller | Scheduler | Standard | SO_ES_3_Hour Event3 |  | 4x0703 | 2.10 | 0 | 23 | Exception 3, 3. event hour
AHU controller | Scheduler | Standard | SO_ES_3_Hour Event4 |  | 4x0704 | 2.10 | 0 | 23 | Exception 3, 4. event hour
AHU controller | Scheduler | Standard | SO_ES_3_Hour Event5 |  | 4x0705 | 2.10 | 0 | 23 | Exception 3, 5. event hour
AHU controller | Scheduler | Standard | SO_ES_3_Hour Event6 |  | 4x0706 | 2.10 | 0 | 23 | Exception 3, 6. event hour
AHU controller | Scheduler | Standard | SO_ES_3_Minute Event1 |  | 4x0707 | 2.10 | 0 | 59 | Exception 3, 1. event minute
AHU controller | Scheduler | Standard | SO_ES_3_Minute Event2 |  | 4x0708 | 2.10 | 0 | 59 | Exception 3, 2. event minute
AHU controller | Scheduler | Standard | SO_ES_3_Minute Event3 |  | 4x0709 | 2.10 | 0 | 59 | Exception 3, 3. event minute
AHU controller | Scheduler | Standard | SO_ES_3_Minute Event4 |  | 4x0710 | 2.10 | 0 | 59 | Exception 3, 4. event minute
AHU controller | Scheduler | Standard | SO_ES_3_Minute Event5 |  | 4x0711 | 2.10 | 0 | 59 | Exception 3, 5. event minute
AHU controller | Scheduler | Standard | SO_ES_3_Minute Event6 |  | 4x0712 | 2.10 | 0 | 59 | Exception 3, 6. event minute
AHU controller | Scheduler | Standard | SO_ES_3_Value Event1 |  | 4x0713 | 2.10 | 0 | 6 | Exception 3, 1. event, 0-Off, 6-Fallback , 1-Stop, 2-Low, 3-Med, 4-High, 5-Extended stop
AHU controller | Scheduler | Standard | SO_ES_3_Value Event2 |  | 4x0714 | 2.10 | 0 | 6 | Exception 3, 2. event, 0-Off, 6-Fallback , 1-Stop, 2-Low, 3-Med, 4-High, 5-Extended stop
AHU controller | Scheduler | Standard | SO_ES_3_Value Event3 |  | 4x0715 | 2.10 | 0 | 6 | Exception 3, 3. event, 0-Off, 6-Fallback , 1-Stop, 2-Low, 3-Med, 4-High, 5-Extended stop
AHU controller | Scheduler | Standard | SO_ES_3_Value Event4 |  | 4x0716 | 2.10 | 0 | 6 | Exception 3, 4. event, 0-Off, 6-Fallback , 1-Stop, 2-Low, 3-Med, 4-High, 5-Extended stop
AHU controller | Scheduler | Standard | SO_ES_3_Value Event5 |  | 4x0717 | 2.10 | 0 | 6 | Exception 3, 5. event, 0-Off, 6-Fallback , 1-Stop, 2-Low, 3-Med, 4-High, 5-Extended stop
AHU controller | Scheduler | Standard | SO_ES_3_Value Event6 |  | 4x0718 | 2.10 | 0 | 6 | Exception 3, 6. event, 0-Off, 6-Fallback , 1-Stop, 2-Low, 3-Med, 4-High, 5-Extended stop
AHU controller | Scheduler | Standard | SO_DefaultValue |  | 4x0719 | 2.10 | 1 | 5 | FallBack speed (Properties) , 1-Stop1, 2-Low, 3-Med, 4-High, 5-Ext.Stop
AHU controller | Scheduler | Standard | CO_DL_1_StartYear CODL1 |  | 4x0720 | 2.10 | 2000 | 2099 | Exception 1, Start Year, Active days 1
AHU controller | Scheduler | Standard | CO_DL_1_StartYear CODL2 |  | 4x0721 | 2.10 | 2000 | 2099 | Exception 1, Start Year, Active days 2
AHU controller | Scheduler | Standard | CO_DL_1_StartYear CODL3 |  | 4x0722 | 2.10 | 2000 | 2099 | Exception 1, Start Year, Active days 3
AHU controller | Scheduler | Standard | CO_DL_1_StartYear CODL4 |  | 4x0723 | 2.10 | 2000 | 2099 | Exception 1, Start Year, Active says 4
AHU controller | Scheduler | Standard | CO_DL_1_StartYear CODL5 |  | 4x0724 | 2.10 | 2000 | 2099 | Exception 1, Start Year, Active days 5
AHU controller | Scheduler | Standard | CO_DL_1_StartYear CODL6 |  | 4x0725 | 2.10 | 2000 | 2099 | Exception 1, Start Year, Active days 6
AHU controller | Scheduler | Standard | CO_DL_1_StartYear CODL7 |  | 4x0726 | 2.10 | 2000 | 2099 | Exception 1, Start Year, Active days 7
AHU controller | Scheduler | Standard | CO_DL_1_StartYear CODL8 |  | 4x0727 | 2.10 | 2000 | 2099 | Exception 1, Start Year, Active days 8
AHU controller | Scheduler | Standard | CO_DL_1_StartYear CODL9 |  | 4x0728 | 2.10 | 2000 | 2099 | Exception 1, Start Year, Active days 9
AHU controller | Scheduler | Standard | CO_DL_1_StartYear CODL10 |  | 4x0729 | 2.10 | 2000 | 2099 | Exception 1, Start Year, Active days 10
AHU controller | Scheduler | Standard | CO_DL_1_StartMonth CODL1 |  | 4x0730 | 2.10 | 0 | 14 | Exception 1, Start Month, Active days 1: 0-Every, 13-odd month, 14-even month
AHU controller | Scheduler | Standard | CO_DL_1_StartMonth CODL2 |  | 4x0731 | 2.10 | 0 | 14 | Exception 1, Start Month, Active days 2: 0-Every, 13-odd month, 14-even month
AHU controller | Scheduler | Standard | CO_DL_1_StartMonth CODL3 |  | 4x0732 | 2.10 | 0 | 14 | Exception 1, Start Month, Active days 3: 0-Every, 13-odd month, 14-even month
AHU controller | Scheduler | Standard | CO_DL_1_StartMonth CODL4 |  | 4x0733 | 2.10 | 0 | 14 | Exception 1, Start Month, Active days 4: 0-Every, 13-odd month, 14-even month
AHU controller | Scheduler | Standard | CO_DL_1_StartMonth CODL5 |  | 4x0734 | 2.10 | 0 | 14 | Exception 1, Start Month, Active days 5: 0-Every, 13-odd month, 14-even month
AHU controller | Scheduler | Standard | CO_DL_1_StartMonth CODL6 |  | 4x0735 | 2.10 | 0 | 14 | Exception 1, Start Month, Active days 6: 0-Every, 13-odd month, 14-even month
AHU controller | Scheduler | Standard | CO_DL_1_StartMonth CODL7 |  | 4x0736 | 2.10 | 0 | 14 | Exception 1, Start Month, Active days 7: 0-Every, 13-odd month, 14-even month
AHU controller | Scheduler | Standard | CO_DL_1_StartMonth CODL8 |  | 4x0737 | 2.10 | 0 | 14 | Exception 1, Start Month, Active days 8: 0-Every, 13-odd month, 14-even month
AHU controller | Scheduler | Standard | CO_DL_1_StartMonth CODL9 |  | 4x0738 | 2.10 | 0 | 14 | Exception 1, Start Month, Active days 9: 0-Every, 13-odd month, 14-even month
AHU controller | Scheduler | Standard | CO_DL_1_StartMonth CODL10 |  | 4x0739 | 2.10 | 0 | 14 | Exception 1, Start Month, Active days 10. 0-Every, 13-odd month, 14-even month
AHU controller | Scheduler | Standard | CO_DL_1_StartDate CODL1 |  | 4x0740 | 2.10 | 0 | CO_DL_1_MaxStartDate | Exception 1, Start date, Active days 1: | 0-Every -------------------Max = 34-------------- 32-Last day of month 33-odd days of month 34-even days of month -------------------Max = 6---------------- 1-days numbered 1..7 2-days numbered 8..14 3-days numbered 15..21 4-days numbered 22.28 5-days numbered 29..31 6-last 7 daus of month
AHU controller | Scheduler | Standard | CO_DL_1_StartDate CODL2 |  | 4x0741 | 2.10 | 0 | CO_DL_1_MaxStartDate | Exception 1, Start date, Active days 2:
AHU controller | Scheduler | Standard | CO_DL_1_StartDate CODL3 |  | 4x0742 | 2.10 | 0 | CO_DL_1_MaxStartDate | Exception 1, Start date, Active days 3:
AHU controller | Scheduler | Standard | CO_DL_1_StartDate CODL4 |  | 4x0743 | 2.10 | 0 | CO_DL_1_MaxStartDate | Exception 1, Start date, Active days 4:
AHU controller | Scheduler | Standard | CO_DL_1_StartDate CODL5 |  | 4x0744 | 2.10 | 0 | CO_DL_1_MaxStartDate | Exception 1, Start date, Active days 5:
AHU controller | Scheduler | Standard | CO_DL_1_StartDate CODL6 |  | 4x0745 | 2.10 | 0 | CO_DL_1_MaxStartDate | Exception 1, Start date, Active days 6:
AHU controller | Scheduler | Standard | CO_DL_1_StartDate CODL7 |  | 4x0746 | 2.10 | 0 | CO_DL_1_MaxStartDate | Exception 1, Start date, Active days 7:
AHU controller | Scheduler | Standard | CO_DL_1_StartDate CODL8 |  | 4x0747 | 2.10 | 0 | CO_DL_1_MaxStartDate | Exception 1, Start date, Active days 8:
AHU controller | Scheduler | Standard | CO_DL_1_StartDate CODL9 |  | 4x0748 | 2.10 | 0 | CO_DL_1_MaxStartDate | Exception 1, Start date, Active days 9:
AHU controller | Scheduler | Standard | CO_DL_1_StartDate CODL10 |  | 4x0749 | 2.10 | 0 | CO_DL_1_MaxStartDate | Exception 1, Start date, Active days 10:
AHU controller | Scheduler | Standard | CO_DL_1_StartWeekday CODL1 |  | 4x0750 | 2.10 | 0 | 7 | Exception 1, Start Weekday: Week Active days 1. 0-Unspecified, 1..7 = Monday..Sunday
AHU controller | Scheduler | Standard | CO_DL_1_StartWeekday CODL2 |  | 4x0751 | 2.10 | 0 | 7 | Exception 1, Start Weekday, Week Active days 2: 0-Unspecified, 1..7 = Monday..Sunday
AHU controller | Scheduler | Standard | CO_DL_1_StartWeekday CODL3 |  | 4x0752 | 2.10 | 0 | 7 | Exception 1, Start Weekday: Week Active days 3. 0-Unspecified, 1..7 = Monday..Sunday
AHU controller | Scheduler | Standard | CO_DL_1_StartWeekday CODL4 |  | 4x0753 | 2.10 | 0 | 7 | Exception 1, Start Weekday, Week Active days 4: 0-Unspecified, 1..7 = Monday..Sunday
AHU controller | Scheduler | Standard | CO_DL_1_StartWeekday CODL5 |  | 4x0754 | 2.10 | 0 | 7 | Exception 1, Start Weekday: Week Active days 5. 0-Unspecified, 1..7 = Monday..Sunday
AHU controller | Scheduler | Standard | CO_DL_1_StartWeekday CODL6 |  | 4x0755 | 2.10 | 0 | 7 | Exception 1, Start Weekday,:Week Active days 6 0-Unspecified, 1..7 = Monday..Sunday
AHU controller | Scheduler | Standard | CO_DL_1_StartWeekday CODL7 |  | 4x0756 | 2.10 | 0 | 7 | Exception 1, Start Weekday, Week Active days 7: 0-Unspecified, 1..7 = Monday..Sunday
AHU controller | Scheduler | Standard | CO_DL_1_StartWeekday CODL8 |  | 4x0757 | 2.10 | 0 | 7 | Exception 1, Start Weekday: Week Active days 8. 0-Unspecified, 1..7 = Monday..Sunday
AHU controller | Scheduler | Standard | CO_DL_1_StartWeekday CODL9 |  | 4x0758 | 2.10 | 0 | 7 | Exception 1, Start Weekday: Week Active days 9. 0-Unspecified, 1..7 = Monday..Sunday
AHU controller | Scheduler | Standard | CO_DL_1_StartWeekday CODL10 |  | 4x0759 | 2.10 | 0 | 7 | Exception 1, Start Weekday: Week Active days 10. 0-Unspecified, 1..7 = Monday..Sunday
AHU controller | Scheduler | Standard | CO_DL_1_StopYear CODL1 |  | 4x0760 | 2.10 | 2000 | 2099 | Exception 1, Stop Year, Period Active days 1
AHU controller | Scheduler | Standard | CO_DL_1_StopYear CODL2 |  | 4x0761 | 2.10 | 2000 | 2099 | Exception 1, Stop Year, Period Active days 2
AHU controller | Scheduler | Standard | CO_DL_1_StopYear CODL3 |  | 4x0762 | 2.10 | 2000 | 2099 | Exception 1, Stop Year, Period Active days 3
AHU controller | Scheduler | Standard | CO_DL_1_StopYear CODL4 |  | 4x0763 | 2.10 | 2000 | 2099 | Exception 1, Stop Year, Period Active days 4
AHU controller | Scheduler | Standard | CO_DL_1_StopYear CODL5 |  | 4x0764 | 2.10 | 2000 | 2099 | Exception 1, Stop Year, Period Active days 5
AHU controller | Scheduler | Standard | CO_DL_1_StopYear CODL6 |  | 4x0765 | 2.10 | 2000 | 2099 | Exception 1, Stop Year, Period Active days 6
AHU controller | Scheduler | Standard | CO_DL_1_StopYear CODL7 |  | 4x0766 | 2.10 | 2000 | 2099 | Exception 1, Stop Year, Period Active days 7
AHU controller | Scheduler | Standard | CO_DL_1_StopYear CODL8 |  | 4x0767 | 2.10 | 2000 | 2099 | Exception 1, Stop Year, Period Active days 8
AHU controller | Scheduler | Standard | CO_DL_1_StopYear CODL9 |  | 4x0768 | 2.10 | 2000 | 2099 | Exception 1, Stop Year, Period Active days 9
AHU controller | Scheduler | Standard | CO_DL_1_StopYear CODL10 |  | 4x0769 | 2.10 | 2000 | 2099 | Exception 1, Stop Year, Period Active days 10
AHU controller | Scheduler | Standard | CO_DL_1_StopMonth CODL1 |  | 4x0770 | 2.10 | 0 | 14 | Exception 1 Stop month Period Active days 1 0-Every, 13-odd month, 14-even month
AHU controller | Scheduler | Standard | CO_DL_1_StopMonth CODL2 |  | 4x0771 | 2.10 | 0 | 14 | Exception 1 Stop month Period Active days 2 0-Every, 13-odd month, 14-even month
AHU controller | Scheduler | Standard | CO_DL_1_StopMonth CODL3 |  | 4x0772 | 2.10 | 0 | 14 | Exception 1 Stop month Period Active days 3 0-Every, 13-odd month, 14-even month
AHU controller | Scheduler | Standard | CO_DL_1_StopMonth CODL4 |  | 4x0773 | 2.10 | 0 | 14 | Exception 1 Stop month Period Active days 4 0-Every, 13-odd month, 14-even month
AHU controller | Scheduler | Standard | CO_DL_1_StopMonth CODL5 |  | 4x0774 | 2.10 | 0 | 14 | Exception 1 Stop month Period Active days 5 0-Every, 13-odd month, 14-even month
AHU controller | Scheduler | Standard | CO_DL_1_StopMonth CODL6 |  | 4x0775 | 2.10 | 0 | 14 | Exception 1 Stop month Period Active days 6 0-Every, 13-odd month, 14-even month
AHU controller | Scheduler | Standard | CO_DL_1_StopMonth CODL7 |  | 4x0776 | 2.10 | 0 | 14 | Exception 1 Stop month Period Active days 7 0-Every, 13-odd month, 14-even month
AHU controller | Scheduler | Standard | CO_DL_1_StopMonth CODl8 |  | 4x0777 | 2.10 | 0 | 14 | Exception 1 Stop month Period Active days 8 0-Every, 13-odd month, 14-even month
AHU controller | Scheduler | Standard | CO_DL_1_StopMonth CODL9 |  | 4x0778 | 2.10 | 0 | 14 | Exception 1 Stop month Period Active days 9 0-Every, 13-odd month, 14-even month
AHU controller | Scheduler | Standard | CO_DL_1_StopMonth CODL10 |  | 4x0779 | 2.10 | 0 | 14 | Exception 1 Stop month Period Active days 10 0-Every, 13-odd month, 14-even month
AHU controller | Scheduler | Standard | CO_DL_1_StopDate CODL1 |  | 4x0780 | 2.10 | 0 | 34 | Exception 1 Stop date Period Active days 1 0-Every, 32-Last day, 33-odd, 34-even day
AHU controller | Scheduler | Standard | CO_DL_1_StopDate CODL2 |  | 4x0781 | 2.10 | 0 | 34 | Exception 1 Stop date Period Active days 2 0-Every, 32-Last day, 33-odd, 34-even day
AHU controller | Scheduler | Standard | CO_DL_1_StopDate CODL3 |  | 4x0782 | 2.10 | 0 | 34 | Exception 1 Stop date Period Active days 3 0-Every, 32-Last day, 33-odd, 34-even day
AHU controller | Scheduler | Standard | CO_DL_1_StopDate CODL4 |  | 4x0783 | 2.10 | 0 | 34 | Exception 1 Stop date Period Active days 4 0-Every, 32-Last day, 33-odd, 34-even day
AHU controller | Scheduler | Standard | CO_DL_1_StopDate CODL5 |  | 4x0784 | 2.10 | 0 | 34 | Exception 1 Stop date Period Active days 5 0-Every, 32-Last day, 33-odd, 34-even day
AHU controller | Scheduler | Standard | CO_DL_1_StopDate CODL6 |  | 4x0785 | 2.10 | 0 | 34 | Exception 1 Stop date Period Active days 6 0-Every, 32-Last day, 33-odd, 34-even day
AHU controller | Scheduler | Standard | CO_DL_1_StopDate CODL7 |  | 4x0786 | 2.10 | 0 | 34 | Exception 1 Stop date Period Active days 7 0-Every, 32-Last day, 33-odd, 34-even day
AHU controller | Scheduler | Standard | CO_DL_1_StopDate CODL8 |  | 4x0787 | 2.10 | 0 | 34 | Exception 1 Stop date Period Active days 8 0-Every, 32-Last day, 33-odd, 34-even day
AHU controller | Scheduler | Standard | CO_DL_1_StopDate CODl9 |  | 4x0788 | 2.10 | 0 | 34 | Exception 1 Stop date Period Active days 9 0-Every, 32-Last day, 33-odd, 34-even day
AHU controller | Scheduler | Standard | CO_DL_1_StopDate CODL10 |  | 4x0789 | 2.10 | 0 | 34 | Exception 1 Stop date Period Active days 10 0-Every, 32-Last day, 33-odd, 34-even day
AHU controller | Scheduler | Standard | CO_DL_1_StopWeekday0 |  | 4x0790 | 2.10 | 0 | 7 | 0-Unspecified, 1..7 = Monday..Sunday. NOTE: SELF CALCULATING..!!
AHU controller | Scheduler | Standard | CO_DL_1_StopWeekday1 |  | 4x0791 | 2.10 | 0 | 7
AHU controller | Scheduler | Standard | CO_DL_1_StopWeekday2 |  | 4x0792 | 2.10 | 0 | 7
AHU controller | Scheduler | Standard | CO_DL_1_StopWeekday3 |  | 4x0793 | 2.10 | 0 | 7
AHU controller | Scheduler | Standard | CO_DL_1_StopWeekday4 |  | 4x0794 | 2.10 | 0 | 7
AHU controller | Scheduler | Standard | CO_DL_1_StopWeekday5 |  | 4x0795 | 2.10 | 0 | 7
AHU controller | Scheduler | Standard | CO_DL_1_StopWeekday6 |  | 4x0796 | 2.10 | 0 | 7
AHU controller | Scheduler | Standard | CO_DL_1_StopWeekday7 |  | 4x0797 | 2.10 | 0 | 7
AHU controller | Scheduler | Standard | CO_DL_1_StopWeekday8 |  | 4x0798 | 2.10 | 0 | 7
AHU controller | Scheduler | Standard | CO_DL_1_StopWeekday9 |  | 4x0799 | 2.10 | 0 | 7
AHU controller | Scheduler | Standard | CO_DL_1_Period CODL1 |  | 4x0800 | 2.10 | 0 | 3 | Exeption 1. Active days 1 selected 0-Date 1-Period 2-Week 3-Inactive | 0-Date (MaxStartDate = 34) 1-Date range (MaxStartDate = 34) 2-Weekday (MaxStartDate = 6) 3-Inactive (MaxStartDate unchanged)
AHU controller | Scheduler | Standard | CO_DL_1_Period CODL2 |  | 4x0801 | 2.10 | 0 | 3 | Exeption 1. Active days 2 selected 0-Date 1-Period 2-Week 3-Inactive
AHU controller | Scheduler | Standard | CO_DL_1_Period CODL3 |  | 4x0802 | 2.10 | 0 | 3 | Exeption 1. Active days 3 selected 0-Date 1-Period 2-Week 3-Inactive
AHU controller | Scheduler | Standard | CO_DL_1_Period CODL4 |  | 4x0803 | 2.10 | 0 | 3 | Exeption 1. Active days 4 selected 0-Date 1-Period 2-Week 3-Inactive
AHU controller | Scheduler | Standard | CO_DL_1_Period CODL5 |  | 4x0804 | 2.10 | 0 | 3 | Exeption 1. Active days 5 selected 0-Date 1-Period 2-Week 3-Inactive
AHU controller | Scheduler | Standard | CO_DL_1_Period CODL6 |  | 4x0805 | 2.10 | 0 | 3 | Exeption 1. Active days 6 selected 0-Date 1-Period 2-Week 3-Inactive
AHU controller | Scheduler | Standard | CO_DL_1_Period CODL7 |  | 4x0806 | 2.10 | 0 | 3 | Exeption 1. Active days 7 selected 0-Date 1-Period 2-Week 3-Inactive
AHU controller | Scheduler | Standard | CO_DL_1_Period CODL8 |  | 4x0807 | 2.10 | 0 | 3 | Exeption 1. Active days 8 selected 0-Date 1-Period 2-Week 3-Inactive
AHU controller | Scheduler | Standard | CO_DL_1_Period CODL9 |  | 4x0808 | 2.10 | 0 | 3 | Exeption 1. Active days 9 selected 0-Date 1-Period 2-Week 3-Inactive
AHU controller | Scheduler | Standard | CO_DL_1_Period CODL10 |  | 4x0809 | 2.10 | 0 | 3 | Exeption 1. Active days 10 selected 0-Date 1-Period 2-Week 3-Inactive
AHU controller | Scheduler | Standard | CO_DL_2_StartYear CODL1 |  | 4x0810 | 2.10 | 2000 | 2099 | Exception 2, Start Year, Active days 1
AHU controller | Scheduler | Standard | CO_DL_2_StartYear CODL2 |  | 4x0811 | 2.10 | 2000 | 2099 | Exception 2, Start Year, Active days 2
AHU controller | Scheduler | Standard | CO_DL_2_StartYear CODL3 |  | 4x0812 | 2.10 | 2000 | 2099 | Exception 2, Start Year, Active days 3
AHU controller | Scheduler | Standard | CO_DL_2_StartYear CODL4 |  | 4x0813 | 2.10 | 2000 | 2099 | Exception 2, Start Year, Active says 4
AHU controller | Scheduler | Standard | CO_DL_2_StartYear CODL5 |  | 4x0814 | 2.10 | 2000 | 2099 | Exception 2, Start Year, Active days 5
AHU controller | Scheduler | Standard | CO_DL_2_StartYear CODL6 |  | 4x0815 | 2.10 | 2000 | 2099 | Exception 2, Start Year, Active days 6
AHU controller | Scheduler | Standard | CO_DL_2_StartYear CODL7 |  | 4x0816 | 2.10 | 2000 | 2099 | Exception 2, Start Year, Active days 7
AHU controller | Scheduler | Standard | CO_DL_2_StartYear CODL8 |  | 4x0817 | 2.10 | 2000 | 2099 | Exception 2, Start Year, Active days 8
AHU controller | Scheduler | Standard | CO_DL_2_StartYear CODL9 |  | 4x0818 | 2.10 | 2000 | 2099 | Exception 2, Start Year, Active days 9
AHU controller | Scheduler | Standard | CO_DL_2_StartYear CODl10 |  | 4x0819 | 2.10 | 2000 | 2099 | Exception 2, Start Year, Active days 10
AHU controller | Scheduler | Standard | CO_DL_2_StartMonth CODL1 |  | 4x0820 | 2.10 | 0 | 14 | Exception 2, Start Month, Active days 1: 0-Every, 13-odd month, 14-even month
AHU controller | Scheduler | Standard | CO_DL_2_StartMonth CODL2 |  | 4x0821 | 2.10 | 0 | 14 | Exception 2, Start Month, Active days 2: 0-Every, 13-odd month, 14-even month
AHU controller | Scheduler | Standard | CO_DL_2_StartMonth CODL3 |  | 4x0822 | 2.10 | 0 | 14 | Exception 2, Start Month, Active days 3: 0-Every, 13-odd month, 14-even month
AHU controller | Scheduler | Standard | CO_DL_2_StartMonth CODL4 |  | 4x0823 | 2.10 | 0 | 14 | Exception 2, Start Month, Active days 4: 0-Every, 13-odd month, 14-even month
AHU controller | Scheduler | Standard | CO_DL_2_StartMonth CODL5 |  | 4x0824 | 2.10 | 0 | 14 | Exception 2, Start Month, Active days 5: 0-Every, 13-odd month, 14-even month
AHU controller | Scheduler | Standard | CO_DL_2_StartMonth CODL6 |  | 4x0825 | 2.10 | 0 | 14 | Exception 2, Start Month, Active days 6: 0-Every, 13-odd month, 14-even month
AHU controller | Scheduler | Standard | CO_DL_2_StartMonth CODL7 |  | 4x0826 | 2.10 | 0 | 14 | Exception 2, Start Month, Active days 7: 0-Every, 13-odd month, 14-even month
AHU controller | Scheduler | Standard | CO_DL_2_StartMonth CODL8 |  | 4x0827 | 2.10 | 0 | 14 | Exception 2, Start Month, Active days 8: 0-Every, 13-odd month, 14-even month
AHU controller | Scheduler | Standard | CO_DL_2_StartMonth CODL9 |  | 4x0828 | 2.10 | 0 | 14 | Exception 2, Start Month, Active days 9: 0-Every, 13-odd month, 14-even month
AHU controller | Scheduler | Standard | CO_DL_2_StartMonth CODL10 |  | 4x0829 | 2.10 | 0 | 14 | Exception 2, Start Month, Active days 10. 0-Every, 13-odd month, 14-even month
AHU controller | Scheduler | Standard | CO_DL_2_StartDate CODL1 |  | 4x0830 | 2.10 | 0 | CO_DL_2_MaxStartDate | Exception 2, Start date, Active days 1: | 0-Every -------------------Max = 34-------------- 32-Last day of month 33-odd days of month 34-even days of month -------------------Max = 6---------------- 1-days numbered 1..7 2-days numbered 8..14 3-days numbered 15..21 4-days numbered 22.28 5-days numbered 29..31 6-last 7 daus of month
AHU controller | Scheduler | Standard | CO_DL_2_StartDate CODL2 |  | 4x0831 | 2.10 | 0 | CO_DL_2_MaxStartDate | Exception 2, Start date, Active days 2:
AHU controller | Scheduler | Standard | CO_DL_2_StartDate CODL3 |  | 4x0832 | 2.10 | 0 | CO_DL_2_MaxStartDate | Exception 2, Start date, Active days 3:
AHU controller | Scheduler | Standard | CO_DL_2_StartDate CODL4 |  | 4x0833 | 2.10 | 0 | CO_DL_2_MaxStartDate | Exception 2, Start date, Active days 4:
AHU controller | Scheduler | Standard | CO_DL_2_StartDate CODL5 |  | 4x0834 | 2.10 | 0 | CO_DL_2_MaxStartDate | Exception 2, Start date, Active days 5:
AHU controller | Scheduler | Standard | CO_DL_2_StartDate CODL6 |  | 4x0835 | 2.10 | 0 | CO_DL_2_MaxStartDate | Exception 2, Start date, Active days 6:
AHU controller | Scheduler | Standard | CO_DL_2_StartDate CODL7 |  | 4x0836 | 2.10 | 0 | CO_DL_2_MaxStartDate | Exception 2, Start date, Active days 7:
AHU controller | Scheduler | Standard | CO_DL_2_StartDate CODL8 |  | 4x0837 | 2.10 | 0 | CO_DL_2_MaxStartDate | Exception 2, Start date, Active days 8:
AHU controller | Scheduler | Standard | CO_DL_2_StartDate CODL9 |  | 4x0838 | 2.10 | 0 | CO_DL_2_MaxStartDate | Exception 2, Start date, Active days 9:
AHU controller | Scheduler | Standard | CO_DL_2_StartDate CODL10 |  | 4x0839 | 2.10 | 0 | CO_DL_2_MaxStartDate | Exception 2, Start date, Active days 10:
AHU controller | Scheduler | Standard | CO_DL_2_StartWeekday CODL1 |  | 4x0840 | 2.10 | 0 | 7 | Exception 2, Start Week Weekday: Active days 1. 0-Unspecified, 1..7 = Monday..Sunday
AHU controller | Scheduler | Standard | CO_DL_2_StartWeekday CODL2 |  | 4x0841 | 2.10 | 0 | 7 | Exception 2, Start Week Weekday, Active days 2: 0-Unspecified, 1..7 = Monday..Sunday
AHU controller | Scheduler | Standard | CO_DL_2_StartWeekday CODL3 |  | 4x0842 | 2.10 | 0 | 7 | Exception 2, Start Week Weekday: Active days 3. 0-Unspecified, 1..7 = Monday..Sunday
AHU controller | Scheduler | Standard | CO_DL_2_StartWeekday CODL4 |  | 4x0843 | 2.10 | 0 | 7 | Exception 2, Start Week Weekday, Active days 4: 0-Unspecified, 1..7 = Monday..Sunday
AHU controller | Scheduler | Standard | CO_DL_2_StartWeekday CODL5 |  | 4x0844 | 2.10 | 0 | 7 | Exception 2, Start Week Weekday: Active days 5. 0-Unspecified, 1..7 = Monday..Sunday
AHU controller | Scheduler | Standard | CO_DL_2_StartWeekday CODL6 |  | 4x0845 | 2.10 | 0 | 7 | Exception 2, Start Week Weekday,:Active days 6 0-Unspecified, 1..7 = Monday..Sunday
AHU controller | Scheduler | Standard | CO_DL_2_StartWeekday CODL7 |  | 4x0846 | 2.10 | 0 | 7 | Exception 2, Start Week Weekday, Active days 7: 0-Unspecified, 1..7 = Monday..Sunday
AHU controller | Scheduler | Standard | CO_DL_2_StartWeekday CODL8 |  | 4x0847 | 2.10 | 0 | 7 | Exception 2, Start Week Weekday: Active days 8. 0-Unspecified, 1..7 = Monday..Sunday
AHU controller | Scheduler | Standard | CO_DL_2_StartWeekday CODL9 |  | 4x0848 | 2.10 | 0 | 7 | Exception 2, Start Week Weekday: Active days 9. 0-Unspecified, 1..7 = Monday..Sunday
AHU controller | Scheduler | Standard | CO_DL_2_StartWeekday CODL10 |  | 4x0849 | 2.10 | 0 | 7 | Exception 2, Start Week Weekday: Active days 10. 0-Unspecified, 1..7 = Monday..Sunday
AHU controller | Scheduler | Standard | CO_DL_2_StopYear CODL1 |  | 4x0850 | 2.10 | 2000 | 2099 | Exception 2, Stop Year, Period Active days 1
AHU controller | Scheduler | Standard | CO_DL_2_StopYear CODL2 |  | 4x0851 | 2.10 | 2000 | 2099 | Exception 2, Stop Year, Period Active days 2
AHU controller | Scheduler | Standard | CO_DL_2_StopYear CODL3 |  | 4x0852 | 2.10 | 2000 | 2099 | Exception 2, Stop Year, Period Active days 3
AHU controller | Scheduler | Standard | CO_DL_2_StopYear CODL4 |  | 4x0853 | 2.10 | 2000 | 2099 | Exception 2, Stop Year, Period Active days 4
AHU controller | Scheduler | Standard | CO_DL_2_StopYear CODL5 |  | 4x0854 | 2.10 | 2000 | 2099 | Exception 2, Stop Year, Period Active days 5
AHU controller | Scheduler | Standard | CO_DL_2_StopYear CODL6 |  | 4x0855 | 2.10 | 2000 | 2099 | Exception 2, Stop Year, Period Active days 6
AHU controller | Scheduler | Standard | CO_DL_2_StopYear CODL7 |  | 4x0856 | 2.10 | 2000 | 2099 | Exception 2, Stop Year, Period Active days 7
AHU controller | Scheduler | Standard | CO_DL_2_StopYear CODL8 |  | 4x0857 | 2.10 | 2000 | 2099 | Exception 2, Stop Year, Period Active days 8
AHU controller | Scheduler | Standard | CO_DL_2_StopYear CODL9 |  | 4x0858 | 2.10 | 2000 | 2099 | Exception 2, Stop Year, Period Active days 9
AHU controller | Scheduler | Standard | CO_DL_2_StopYear CODL10 |  | 4x0859 | 2.10 | 2000 | 2099 | Exception 2, Stop Year, Period Active days 10
AHU controller | Scheduler | Standard | CO_DL_2_StopMonth CODl1 |  | 4x0860 | 2.10 | 0 | 14 | Exception 2 Stop month Period Active days 1 0-Every, 13-odd month, 14-even month
AHU controller | Scheduler | Standard | CO_DL_2_StopMonth CODL2 |  | 4x0861 | 2.10 | 0 | 14 | Exception 2 Stop month Period Active days 2 0-Every, 13-odd month, 14-even month
AHU controller | Scheduler | Standard | CO_DL_2_StopMonth CODL3 |  | 4x0862 | 2.10 | 0 | 14 | Exception 2 Stop month Period Active days 3 0-Every, 13-odd month, 14-even month
AHU controller | Scheduler | Standard | CO_DL_2_StopMonth CODL4 |  | 4x0863 | 2.10 | 0 | 14 | Exception 2 Stop month Period Active days 4 0-Every, 13-odd month, 14-even month
AHU controller | Scheduler | Standard | CO_DL_2_StopMonth CODL5 |  | 4x0864 | 2.10 | 0 | 14 | Exception 2 Stop month Period Active days 5 0-Every, 13-odd month, 14-even month
AHU controller | Scheduler | Standard | CO_DL_2_StopMonth CODL6 |  | 4x0865 | 2.10 | 0 | 14 | Exception 2 Stop month Period Active days 6 0-Every, 13-odd month, 14-even month
AHU controller | Scheduler | Standard | CO_DL_2_StopMonth CODl7 |  | 4x0866 | 2.10 | 0 | 14 | Exception 2 Stop month Period Active days 7 0-Every, 13-odd month, 14-even month
AHU controller | Scheduler | Standard | CO_DL_2_StopMonth CODL8 |  | 4x0867 | 2.10 | 0 | 14 | Exception 2 Stop month Period Active days 8 0-Every, 13-odd month, 14-even month
AHU controller | Scheduler | Standard | CO_DL_2_StopMonth CODL9 |  | 4x0868 | 2.10 | 0 | 14 | Exception 2 Stop month Period Active days 9 0-Every, 13-odd month, 14-even month
AHU controller | Scheduler | Standard | CO_DL_2_StopMonth CODl10 |  | 4x0869 | 2.10 | 0 | 14 | Exception 2 Stop month Period Active days 10 0-Every, 13-odd month, 14-even month
AHU controller | Scheduler | Standard | CO_DL_2_StopDate CODL1 |  | 4x0870 | 2.10 | 0 | 34 | Exception 2 Stop date Period Active days 1 0-Every, 32-Last day, 33-odd, 34-even day
AHU controller | Scheduler | Standard | CO_DL_2_StopDate CODL2 |  | 4x0871 | 2.10 | 0 | 34 | Exception 2 Stop date Period Active days 2 0-Every, 32-Last day, 33-odd, 34-even day
AHU controller | Scheduler | Standard | CO_DL_2_StopDate CODL3 |  | 4x0872 | 2.10 | 0 | 34 | Exception 2 Stop date Period Active days 3 0-Every, 32-Last day, 33-odd, 34-even day
AHU controller | Scheduler | Standard | CO_DL_2_StopDate CODL4 |  | 4x0873 | 2.10 | 0 | 34 | Exception 2 Stop date Period Active days 4 0-Every, 32-Last day, 33-odd, 34-even day
AHU controller | Scheduler | Standard | CO_DL_2_StopDate CODL5 |  | 4x0874 | 2.10 | 0 | 34 | Exception 2 Stop date Period Active days 5 0-Every, 32-Last day, 33-odd, 34-even day
AHU controller | Scheduler | Standard | CO_DL_2_StopDate CODL6 |  | 4x0875 | 2.10 | 0 | 34 | Exception 2 Stop date Period Active days 6 0-Every, 32-Last day, 33-odd, 34-even day
AHU controller | Scheduler | Standard | CO_DL_2_StopDate CODL7 |  | 4x0876 | 2.10 | 0 | 34 | Exception 2 Stop date Period Active days 7 0-Every, 32-Last day, 33-odd, 34-even day
AHU controller | Scheduler | Standard | CO_DL_2_StopDate CODL8 |  | 4x0877 | 2.10 | 0 | 34 | Exception 2 Stop date Period Active days 8 0-Every, 32-Last day, 33-odd, 34-even day
AHU controller | Scheduler | Standard | CO_DL_2_StopDate CODL9 |  | 4x0878 | 2.10 | 0 | 34 | Exception 2 Stop date Period Active days 9 0-Every, 32-Last day, 33-odd, 34-even day
AHU controller | Scheduler | Standard | CO_DL_2_StopDate CODL10 |  | 4x0879 | 2.10 | 0 | 34 | Exception 2 Stop date Period Active days 10 0-Every, 32-Last day, 33-odd, 34-even day
AHU controller | Scheduler | Standard | CO_DL_2_StopWeekday0 |  | 4x0880 | 2.10 | 0 | 7 | 0-Unspecified, 1..7 = Monday..Sunday. NOTE: SELF CALCULATING..!!
AHU controller | Scheduler | Standard | CO_DL_2_StopWeekday1 |  | 4x0881 | 2.10 | 0 | 7
AHU controller | Scheduler | Standard | CO_DL_2_StopWeekday2 |  | 4x0882 | 2.10 | 0 | 7
AHU controller | Scheduler | Standard | CO_DL_2_StopWeekday3 |  | 4x0883 | 2.10 | 0 | 7
AHU controller | Scheduler | Standard | CO_DL_2_StopWeekday4 |  | 4x0884 | 2.10 | 0 | 7
AHU controller | Scheduler | Standard | CO_DL_2_StopWeekday5 |  | 4x0885 | 2.10 | 0 | 7
AHU controller | Scheduler | Standard | CO_DL_2_StopWeekday6 |  | 4x0886 | 2.10 | 0 | 7
AHU controller | Scheduler | Standard | CO_DL_2_StopWeekday7 |  | 4x0887 | 2.10 | 0 | 7
AHU controller | Scheduler | Standard | CO_DL_2_StopWeekday8 |  | 4x0888 | 2.10 | 0 | 7
AHU controller | Scheduler | Standard | CO_DL_2_StopWeekday9 |  | 4x0889 | 2.10 | 0 | 7
AHU controller | Scheduler | Standard | CO_DL_2_Period CODL1 |  | 4x0890 | 2.10 | 0 | 3 | Exeption 2. Active days 1 selected 0-Date 1-Period 2-Week 3-Inactive | 0-Date (MaxStartDate = 34) 1-Date range (MaxStartDate = 34) 2-Weekday (MaxStartDate = 6) 3-Inactive (MaxStartDate unchanged)
AHU controller | Scheduler | Standard | CO_DL_2_Period CODL2 |  | 4x0891 | 2.10 | 0 | 3 | Exeption 2. Active days 2 selected 0-Date 1-Period 2-Week 3-Inactive
AHU controller | Scheduler | Standard | CO_DL_2_Period CODL3 |  | 4x0892 | 2.10 | 0 | 3 | Exeption 2. Active days 3 selected 0-Date 1-Period 2-Week 3-Inactive
AHU controller | Scheduler | Standard | CO_DL_2_Period CODL4 |  | 4x0893 | 2.10 | 0 | 3 | Exeption 2. Active days 4 selected 0-Date 1-Period 2-Week 3-Inactive
AHU controller | Scheduler | Standard | CO_DL_2_Period CODL5 |  | 4x0894 | 2.10 | 0 | 3 | Exeption 2. Active days 5 selected 0-Date 1-Period 2-Week 3-Inactive
AHU controller | Scheduler | Standard | CO_DL_2_Period CODL6 |  | 4x0895 | 2.10 | 0 | 3 | Exeption 2. Active days 6 selected 0-Date 1-Period 2-Week 3-Inactive
AHU controller | Scheduler | Standard | CO_DL_2_Period CODL7 |  | 4x0896 | 2.10 | 0 | 3 | Exeption 2. Active days 7 selected 0-Date 1-Period 2-Week 3-Inactive
AHU controller | Scheduler | Standard | CO_DL_2_Period CODL8 |  | 4x0897 | 2.10 | 0 | 3 | Exeption 2. Active days 8 selected 0-Date 1-Period 2-Week 3-Inactive
AHU controller | Scheduler | Standard | CO_DL_2_Period CODL9 |  | 4x0898 | 2.10 | 0 | 3 | Exeption 2. Active days 9 selected 0-Date 1-Period 2-Week 3-Inactive
AHU controller | Scheduler | Standard | CO_DL_2_Period CODL10 |  | 4x0899 | 2.10 | 0 | 3 | Exeption 2. Active days 10 selected 0-Date 1-Period 2-Week 3-Inactive
AHU controller | Scheduler | Standard | CO_DL_3_StartYear CODL1 |  | 4x0900 | 2.10 | 2000 | 2099 | Exception 3, Start Year, Active days 1
AHU controller | Scheduler | Standard | CO_DL_3_StartYear CODL2 |  | 4x0901 | 2.10 | 2000 | 2099 | Exception 3, Start Year, Active days 2
AHU controller | Scheduler | Standard | CO_DL_3_StartYear CODL3 |  | 4x0902 | 2.10 | 2000 | 2099 | Exception 3, Start Year, Active days 3
AHU controller | Scheduler | Standard | CO_DL_3_StartYear CODL4 |  | 4x0903 | 2.10 | 2000 | 2099 | Exception 3, Start Year, Active says 4
AHU controller | Scheduler | Standard | CO_DL_3_StartYear CODL5 |  | 4x0904 | 2.10 | 2000 | 2099 | Exception 3, Start Year, Active days 5
AHU controller | Scheduler | Standard | CO_DL_3_StartYear CODL6 |  | 4x0905 | 2.10 | 2000 | 2099 | Exception 3, Start Year, Active days 6
AHU controller | Scheduler | Standard | CO_DL_3_StartYear CODL7 |  | 4x0906 | 2.10 | 2000 | 2099 | Exception 3, Start Year, Active days 7
AHU controller | Scheduler | Standard | CO_DL_3_StartYear CODL8 |  | 4x0907 | 2.10 | 2000 | 2099 | Exception 3, Start Year, Active days 8
AHU controller | Scheduler | Standard | CO_DL_3_StartYear CODL9 |  | 4x0908 | 2.10 | 2000 | 2099 | Exception 3, Start Year, Active days 9
AHU controller | Scheduler | Standard | CO_DL_3_StartYear CODL10 |  | 4x0909 | 2.10 | 2000 | 2099 | Exception 3, Start Year, Active days 10
AHU controller | Scheduler | Standard | CO_DL_3_StartMonth CODL1 |  | 4x0910 | 2.10 | 0 | 14 | Exception 3, Start Month, Active days 1: 0-Every, 13-odd month, 14-even month
AHU controller | Scheduler | Standard | CO_DL_3_StartMonth CODL2 |  | 4x0911 | 2.10 | 0 | 14 | Exception 3, Start Month, Active days 2: 0-Every, 13-odd month, 14-even month
AHU controller | Scheduler | Standard | CO_DL_3_StartMonth CODL3 |  | 4x0912 | 2.10 | 0 | 14 | Exception 3, Start Month, Active days 3: 0-Every, 13-odd month, 14-even month
AHU controller | Scheduler | Standard | CO_DL_3_StartMonth CODL4 |  | 4x0913 | 2.10 | 0 | 14 | Exception 3, Start Month, Active days 4: 0-Every, 13-odd month, 14-even month
AHU controller | Scheduler | Standard | CO_DL_3_StartMonth CODL5 |  | 4x0914 | 2.10 | 0 | 14 | Exception 3, Start Month, Active days 5: 0-Every, 13-odd month, 14-even month
AHU controller | Scheduler | Standard | CO_DL_3_StartMonth CODL6 |  | 4x0915 | 2.10 | 0 | 14 | Exception 3, Start Month, Active days 6: 0-Every, 13-odd month, 14-even month
AHU controller | Scheduler | Standard | CO_DL_3_StartMonth CODL7 |  | 4x0916 | 2.10 | 0 | 14 | Exception 3, Start Month, Active days 7: 0-Every, 13-odd month, 14-even month
AHU controller | Scheduler | Standard | CO_DL_3_StartMonth CODL8 |  | 4x0917 | 2.10 | 0 | 14 | Exception 3, Start Month, Active days 8: 0-Every, 13-odd month, 14-even month
AHU controller | Scheduler | Standard | CO_DL_3_StartMonth CODL9 |  | 4x0918 | 2.10 | 0 | 14 | Exception 3, Start Month, Active days 9: 0-Every, 13-odd month, 14-even month
AHU controller | Scheduler | Standard | CO_DL_3_StartMonth CODL10 |  | 4x0919 | 2.10 | 0 | 14 | Exception 3, Start Month, Active days 10. 0-Every, 13-odd month, 14-even month
AHU controller | Scheduler | Standard | CO_DL_3_StartDate CODL1 |  | 4x0920 | 2.10 | 0 | CO_DL_3_MaxStartDate | Exception 3, Start date, Active days 1: | 0-Every -------------------Max = 34-------------- 32-Last day of month 33-odd days of month 34-even days of month -------------------Max = 6---------------- 1-days numbered 1..7 2-days numbered 8..14 3-days numbered 15..21 4-days numbered 22.28 5-days numbered 29..31 6-last 7 daus of month
AHU controller | Scheduler | Standard | CO_DL_3_StartDate CODL2 |  | 4x0921 | 2.10 | 0 | CO_DL_3_MaxStartDate | Exception 3, Start date, Active days 2:
AHU controller | Scheduler | Standard | CO_DL_3_StartDate CODL3 |  | 4x0922 | 2.10 | 0 | CO_DL_3_MaxStartDate | Exception 3, Start date, Active days 3:
AHU controller | Scheduler | Standard | CO_DL_3_StartDate DODL4 |  | 4x0923 | 2.10 | 0 | CO_DL_3_MaxStartDate | Exception 3, Start date, Active days 4:
AHU controller | Scheduler | Standard | CO_DL_3_StartDate CODL5 |  | 4x0924 | 2.10 | 0 | CO_DL_3_MaxStartDate | Exception 3, Start date, Active days 5:
AHU controller | Scheduler | Standard | CO_DL_3_StartDate CODL6 |  | 4x0925 | 2.10 | 0 | CO_DL_3_MaxStartDate | Exception 3, Start date, Active days 6:
AHU controller | Scheduler | Standard | CO_DL_3_StartDate CODL7 |  | 4x0926 | 2.10 | 0 | CO_DL_3_MaxStartDate | Exception 3, Start date, Active days 7:
AHU controller | Scheduler | Standard | CO_DL_3_StartDate CODL8 |  | 4x0927 | 2.10 | 0 | CO_DL_3_MaxStartDate | Exception 3, Start date, Active days 8:
AHU controller | Scheduler | Standard | CO_DL_3_StartDate CODL9 |  | 4x0928 | 2.10 | 0 | CO_DL_3_MaxStartDate | Exception 3, Start date, Active days 9:
AHU controller | Scheduler | Standard | CO_DL_3_StartDate CODL10 |  | 4x0929 | 2.10 | 0 | CO_DL_3_MaxStartDate | Exception 3, Start date, Active days 10:
AHU controller | Scheduler | Standard | CO_DL_3_StartWeekday CODL1 |  | 4x0930 | 2.10 | 0 | 7 | Exception 3, Start Weekday: Active days 1. 0-Unspecified, 1..7 = Monday..Sunday
AHU controller | Scheduler | Standard | CO_DL_3_StartWeekday CODL2 |  | 4x0931 | 2.10 | 0 | 7 | Exception 3, Start Weekday, Active days 2: 0-Unspecified, 1..7 = Monday..Sunday
AHU controller | Scheduler | Standard | CO_DL_3_StartWeekday CODL3 |  | 4x0932 | 2.10 | 0 | 7 | Exception 3, Start Weekday: Active days 3. 0-Unspecified, 1..7 = Monday..Sunday
AHU controller | Scheduler | Standard | CO_DL_3_StartWeekday CODL4 |  | 4x0933 | 2.10 | 0 | 7 | Exception 3, Start Weekday, Active days 4: 0-Unspecified, 1..7 = Monday..Sunday
AHU controller | Scheduler | Standard | CO_DL_3_StartWeekday CODL5 |  | 4x0934 | 2.10 | 0 | 7 | Exception 3, Start Weekday: Active days 5. 0-Unspecified, 1..7 = Monday..Sunday
AHU controller | Scheduler | Standard | CO_DL_3_StartWeekday CODL6 |  | 4x0935 | 2.10 | 0 | 7 | Exception 3, Start Weekday,:Active days 6 0-Unspecified, 1..7 = Monday..Sunday
AHU controller | Scheduler | Standard | CO_DL_3_StartWeekday CODL7 |  | 4x0936 | 2.10 | 0 | 7 | Exception 3, Start Weekday, Active days 7: 0-Unspecified, 1..7 = Monday..Sunday
AHU controller | Scheduler | Standard | CO_DL_3_StartWeekday CODL8 |  | 4x0937 | 2.10 | 0 | 7 | Exception 3, Start Weekday: Active days 8. 0-Unspecified, 1..7 = Monday..Sunday
AHU controller | Scheduler | Standard | CO_DL_3_StartWeekday CODL9 |  | 4x0938 | 2.10 | 0 | 7 | Exception 3, Start Weekday: Active days 9. 0-Unspecified, 1..7 = Monday..Sunday
AHU controller | Scheduler | Standard | CO_DL_3_StartWeekday CODL10 |  | 4x0939 | 2.10 | 0 | 7 | Exception 3, Start Weekday: Active days 10. 0-Unspecified, 1..7 = Monday..Sunday
AHU controller | Scheduler | Standard | CO_DL_3_StopYear CODL1 |  | 4x0940 | 2.10 | 2000 | 2099 | Exception 3, Stop Year, Period Active days 1
AHU controller | Scheduler | Standard | CO_DL_3_StopYear CODL2 |  | 4x0941 | 2.10 | 2000 | 2099 | Exception 3, Stop Year, Period Active days 2
AHU controller | Scheduler | Standard | CO_DL_3_StopYear CODL3 |  | 4x0942 | 2.10 | 2000 | 2099 | Exception 3, Stop Year, Period Active days 3
AHU controller | Scheduler | Standard | CO_DL_3_StopYear CODL4 |  | 4x0943 | 2.10 | 2000 | 2099 | Exception 3, Stop Year, Period Active days 4
AHU controller | Scheduler | Standard | CO_DL_3_StopYear CODL5 |  | 4x0944 | 2.10 | 2000 | 2099 | Exception 3, Stop Year, Period Active days 5
AHU controller | Scheduler | Standard | CO_DL_3_StopYear CODL6 |  | 4x0945 | 2.10 | 2000 | 2099 | Exception 3, Stop Year, Period Active days 6
AHU controller | Scheduler | Standard | CO_DL_3_StopYear CODL7 |  | 4x0946 | 2.10 | 2000 | 2099 | Exception 3, Stop Year, Period Active days 7
AHU controller | Scheduler | Standard | CO_DL_3_StopYear CODL8 |  | 4x0947 | 2.10 | 2000 | 2099 | Exception 3, Stop Year, Period Active days 8
AHU controller | Scheduler | Standard | CO_DL_3_StopYear CODL9 |  | 4x0948 | 2.10 | 2000 | 2099 | Exception 3, Stop Year, Period Active days 9
AHU controller | Scheduler | Standard | CO_DL_3_StopYear CODL10 |  | 4x0949 | 2.10 | 2000 | 2099 | Exception 3, Stop Year, Period Active days 10
AHU controller | Scheduler | Standard | CO_DL_3_StopMonth CODL1 |  | 4x0950 | 2.10 | 0 | 14 | Exception 3 Stop month Period Active days 1 0-Every, 13-odd month, 14-even month
AHU controller | Scheduler | Standard | CO_DL_3_StopMonth CODL2 |  | 4x0951 | 2.10 | 0 | 14 | Exception 3 Stop month Period Active days 2 0-Every, 13-odd month, 14-even month
AHU controller | Scheduler | Standard | CO_DL_3_StopMonth CODL3 |  | 4x0952 | 2.10 | 0 | 14 | Exception 3 Stop month Period Active days 3 0-Every, 13-odd month, 14-even month
AHU controller | Scheduler | Standard | CO_DL_3_StopMonth CODL4 |  | 4x0953 | 2.10 | 0 | 14 | Exception 3 Stop month Period Active days 4 0-Every, 13-odd month, 14-even month
AHU controller | Scheduler | Standard | CO_DL_3_StopMonth CODL5 |  | 4x0954 | 2.10 | 0 | 14 | Exception 3 Stop month Period Active days 5 0-Every, 13-odd month, 14-even month
AHU controller | Scheduler | Standard | CO_DL_3_StopMonth CODL6 |  | 4x0955 | 2.10 | 0 | 14 | Exception 3 Stop month Period Active days 6 0-Every, 13-odd month, 14-even month
AHU controller | Scheduler | Standard | CO_DL_3_StopMonth CODL7 |  | 4x0956 | 2.10 | 0 | 14 | Exception 3 Stop month Period Active days 7 0-Every, 13-odd month, 14-even month
AHU controller | Scheduler | Standard | CO_DL_3_StopMonth CODL8 |  | 4x0957 | 2.10 | 0 | 14 | Exception 3 Stop month Period Active days 8 0-Every, 13-odd month, 14-even month
AHU controller | Scheduler | Standard | CO_DL_3_StopMonth CODL9 |  | 4x0958 | 2.10 | 0 | 14 | Exception 3 Stop month Period Active days 9 0-Every, 13-odd month, 14-even month
AHU controller | Scheduler | Standard | CO_DL_3_StopMonth CODL10 |  | 4x0959 | 2.10 | 0 | 14 | Exception 3 Stop month Period Active days 10 0-Every, 13-odd month, 14-even month
AHU controller | Scheduler | Standard | CO_DL_3_StopDate CODL1 |  | 4x0960 | 2.10 | 0 | 34 | Exception 3 Stop date Period Active days 1 0-Every, 32-Last day, 33-odd, 34-even day
AHU controller | Scheduler | Standard | CO_DL_3_StopDate CODL2 |  | 4x0961 | 2.10 | 0 | 34 | Exception 3 Stop date Period Active days 2 0-Every, 32-Last day, 33-odd, 34-even day
AHU controller | Scheduler | Standard | CO_DL_3_StopDate CODL3 |  | 4x0962 | 2.10 | 0 | 34 | Exception 3 Stop date Period Active days 3 0-Every, 32-Last day, 33-odd, 34-even day
AHU controller | Scheduler | Standard | CO_DL_3_StopDate CODL4 |  | 4x0963 | 2.10 | 0 | 34 | Exception 3 Stop date Period Active days 4 0-Every, 32-Last day, 33-odd, 34-even day
AHU controller | Scheduler | Standard | CO_DL_3_StopDate CODL5 |  | 4x0964 | 2.10 | 0 | 34 | Exception 3 Stop date Period Active days 5 0-Every, 32-Last day, 33-odd, 34-even day
AHU controller | Scheduler | Standard | CO_DL_3_StopDate CODL6 |  | 4x0965 | 2.10 | 0 | 34 | Exception 3 Stop date Period Active days 6 0-Every, 32-Last day, 33-odd, 34-even day
AHU controller | Scheduler | Standard | CO_DL_3_StopDate CODL7 |  | 4x0966 | 2.10 | 0 | 34 | Exception 3 Stop date Period Active days 7 0-Every, 32-Last day, 33-odd, 34-even day
AHU controller | Scheduler | Standard | CO_DL_3_StopDate CODL8 |  | 4x0967 | 2.10 | 0 | 34 | Exception 3 Stop date Period Active days 8 0-Every, 32-Last day, 33-odd, 34-even day
AHU controller | Scheduler | Standard | CO_DL_3_StopDate CODL9 |  | 4x0968 | 2.10 | 0 | 34 | Exception 3 Stop date Period Active days 9 0-Every, 32-Last day, 33-odd, 34-even day
AHU controller | Scheduler | Standard | CO_DL_3_StopDate CODl10 |  | 4x0969 | 2.10 | 0 | 34 | Exception 3 Stop date Period Active days 10 0-Every, 32-Last day, 33-odd, 34-even day
AHU controller | Scheduler | Standard | CO_DL_3_StopWeekday0 |  | 4x0970 | 2.10 | 0 | 7 | 0-Unspecified, 1..7 = Monday..Sunday. NOTE: SELF CALCULATING..!!
AHU controller | Scheduler | Standard | CO_DL_3_StopWeekday1 |  | 4x0971 | 2.10 | 0 | 7
AHU controller | Scheduler | Standard | CO_DL_3_StopWeekday2 |  | 4x0972 | 2.10 | 0 | 7
AHU controller | Scheduler | Standard | CO_DL_3_StopWeekday3 |  | 4x0973 | 2.10 | 0 | 7
AHU controller | Scheduler | Standard | CO_DL_3_StopWeekday4 |  | 4x0974 | 2.10 | 0 | 7
AHU controller | Scheduler | Standard | CO_DL_3_StopWeekday5 |  | 4x0975 | 2.10 | 0 | 7
AHU controller | Scheduler | Standard | CO_DL_3_StopWeekday6 |  | 4x0976 | 2.10 | 0 | 7
AHU controller | Scheduler | Standard | CO_DL_3_StopWeekday7 |  | 4x0977 | 2.10 | 0 | 7
AHU controller | Scheduler | Standard | CO_DL_3_StopWeekday8 |  | 4x0978 | 2.10 | 0 | 7
AHU controller | Scheduler | Standard | CO_DL_3_StopWeekday9 |  | 4x0979 | 2.10 | 0 | 7
AHU controller | Scheduler | Standard | CO_DL_3_Period CODL1 |  | 4x0980 | 2.10 | 0 | 3 | Exeption 3. Active days 1 selected 0-Date 1-Period 2-Week 3-Inactive | 0-Date (MaxStartDate = 34) 1-Date range (MaxStartDate = 34) 2-Weekday (MaxStartDate = 6) 3-Inactive (MaxStartDate unchanged)
AHU controller | Scheduler | Standard | CO_DL_3_Period CODL2 |  | 4x0981 | 2.10 | 0 | 3 | Exeption 3. Active days 2 selected 0-Date 1-Period 2-Week 3-Inactive
AHU controller | Scheduler | Standard | CO_DL_3_Period CODL3 |  | 4x0982 | 2.10 | 0 | 3 | Exeption 3. Active days 3 selected 0-Date 1-Period 2-Week 3-Inactive
AHU controller | Scheduler | Standard | CO_DL_3_Period CODL4 |  | 4x0983 | 2.10 | 0 | 3 | Exeption 3. Active days 4 selected 0-Date 1-Period 2-Week 3-Inactive
AHU controller | Scheduler | Standard | CO_DL_3_Period CODL5 |  | 4x0984 | 2.10 | 0 | 3 | Exeption 3. Active days 5 selected 0-Date 1-Period 2-Week 3-Inactive
AHU controller | Scheduler | Standard | CO_DL_3_Period CODL6 |  | 4x0985 | 2.10 | 0 | 3 | Exeption 3. Active days 6 selected 0-Date 1-Period 2-Week 3-Inactive
AHU controller | Scheduler | Standard | CO_DL_3_Period CODL7 |  | 4x0986 | 2.10 | 0 | 3 | Exeption 3. Active days 7 selected 0-Date 1-Period 2-Week 3-Inactive
AHU controller | Scheduler | Standard | CO_DL_3_Period CODL8 |  | 4x0987 | 2.10 | 0 | 3 | Exeption 3. Active days 8 selected 0-Date 1-Period 2-Week 3-Inactive
AHU controller | Scheduler | Standard | CO_DL_3_Period CODL9 |  | 4x0988 | 2.10 | 0 | 3 | Exeption 3. Active days 9 selected 0-Date 1-Period 2-Week 3-Inactive
AHU controller | Scheduler | Standard | CO_DL_3_Period CODL10 |  | 4x0989 | 2.10 | 0 | 3 | Exeption 3. Active days 10 selected 0-Date 1-Period 2-Week 3-Inactive
© 2023 OJ Electronics A/S · ® The OJ trademark is a registered trademark belonging to OJ Electronics A/S
Note on A1: Jens B. Antonsen: Modbus and BACnet parameters reflect current values on installed components in the actual AHU. The parameters are always present, but might not be active. Actual AHU components installed depends on the AHU manufacturer brand and model.
Note on C1: Jens B. Antonsen: Standard: Always included in OJ-Air2master. Special: Partly included in some private label variants. Check the AHU controller part. No. and the AHU manufactor documentation.
Note on F1: Jens B. Antonsen: Registers start at no. 1. Adresses start at no. 0. A typical mistake is R/W to a neighbour register.
Note on G1: Jens B. Antonsen: Number: Register is available in this software version and higher versions. x.xx: Register is available in this software and some lower versions.
Note on H1: Jens B. Antonsen: Minimum value. Lower values will be ignored.
Note on I1: Jens B. Antonsen: Maximum value. Higher values will be ignored.