## alarmlist00000
Alarmlist, OJ-AHC-3000 SW 2.10 | [5 empty] | HMI alarm text |  | OJ-Air Cloud
Alarm Number | Priority | Alarm- delay sec. | Alarm Limit | Auto reset | Unit stop | Alarm text | Alarm Number | Alarm text
0101 | A | 3 | N/A |  |  | Fire alarm via digital input (From the HMI menu, fans can be setup to fire operation) | 5101 | Fire alarm via digital input (From the HMI menu, fans can be setup to fire operation)
0102 | A | 3 | N/A |  | X | External fire thermostat alarm | 5102 | External fire thermostat alarm
0103 | A | 3 | N/A |  | X | Internal fire alarm (High supply air/extract air temperature) | 5103 | Internal fire alarm (High supply air/extract air temperature)
0104 | A | 3 | N/A |  | X | Extern Firethermostat active | 5104 | Extern Firethermostat active
0201 | A | 3 | N/A | X | X | Supply air DV controller: No communication | 5201 | Supply air DV controller: No communication
0202 | A | 3 | N/A | X | X | Exhaust air DV controller: No communication | 5202 | Exhaust air DV controller: No communication
0205 | A | 3 | N/A | X | X | Extension module EXT 3: No communication | 5205 | Extension module EXT 3: No communication
0206 | A | 3 | N/A | X | X | Extension module EXT 4: No communication | 5206 | Extension module EXT 4: No communication
0212 | A | 3 | N/A | X | X | Rotary heat exchanger (DRHX): No communication | 5212 | Rotary heat exchanger (DRHX): No communication
0214 | A | 3 | N/A | X | X | Pressure transmitter (PTH-1, Pressure outdoor air filter): No communication | 5214 | Pressure transmitter (PTH-1, Pressure outdoor air filter): No communication
0215 | A | 3 | N/A | X | X | Pressure transmitter (PTH-2, Pressure extract air flow): No communication | 5215 | Pressure transmitter (PTH-2, Pressure extract air flow): No communication
0301 | A | 3 | N/A | X | X | Pressure transmitter (PTH-3, Pressure supply air flow): No communication | 5301 | Pressure transmitter (PTH-3, Pressure supply air flow): No communication
0302 | A | 3 | N/A | X | X | Pressure transmitter (PTH-4, Pressure extract air filter): No communication | 5302 | Pressure transmitter (PTH-4, Pressure extract air filter): No communication
0304 | A | 3 | N/A | X | X | Pressure transmitter (PTH-6, Pressure supply air duct): No communication | 5304 | Pressure transmitter (PTH-6, Pressure supply air duct): No communication
0305 | A | 3 | N/A | X | X | Pressure transmitter (PTH-7, Pressure extract air duct): No communication | 5305 | Pressure transmitter (PTH-7, Pressure extract air duct): No communication
0306 | A | 3 | N/A | X | X | Pressure transmitter (PTH-8, Pressure plate-EXC): No communication | 5306 | Pressure transmitter (PTH-8, Pressure plate-EXC): No communication
0311 | A | 3 | N/A | X | X | Pressure transmitter 1 (PTH6202-1, Pressure outdoor air filter and extract air flow ) No communication | 5311 | Pressure transmitter 1 (PTH6202-1, Pressure outdoor air filter and extract air flow ) No communication
0312 | A | 3 | N/A | X | X | Pressure transmitter 2 (PTH6202-2, extract air filter pressure1 and 2) No communication | 5312 | Pressure transmitter 2 (PTH6202-2, extract air filter pressure1 and 2) No communication
0313 | A | 3 | N/A | X | X | Pressure transmitter 3 (PTH6202-3, Pressure extract air and supply air duct) No communication | 5313 | Pressure transmitter 3 (PTH6202-3, Pressure extract air and supply air duct) No communication
0314 | A | 3 | N/A | X | X | Pressure transmitter 4 (PTH6202-4, Pressure extract air filter / outdoor air filter) No communication | 5314 | Pressure transmitter 4 (PTH6202-4, Pressure extract air filter / outdoor air filter) No communication
0315 | A | 3 | N/A | X | X | Pressure transmitter 5 (PTH6202-5, Pressure supply air flow / extract air flow) No communication | 5315 | Pressure transmitter 5 (PTH6202-5, Pressure supply air flow / extract air flow) No communication
0401 | B | 10 | N/A | X |  | Humidity sensor (HTH6202, humidity and temperature): No communication | 5401 | Humidity sensor (HTH6202, humidity and temperature): No communication
0406 | B | 10 | N/A | X |  | Temperature sensor (TTH-6040-O, Outdoor air temperature): No communication | 5406 | Temperature sensor (TTH-6040-O, Outdoor air temperature): No communication
0407 | A | 10 | N/A | X | X | Temperature sensor (TTH-6040-W Room temperature): No communication | 5407 | Temperature sensor (TTH-6040-W Room temperature): No communication
0409 | A | 10 | N/A | X | X | Room control (HMI-20T, Room temperature sensor & touch display): No communication | 5409 | Room control (HMI-20T, Room temperature sensor & touch display): No communication
0501 | A | 3 | N/A |  | X | Supply air controller: Alarm stop | 5501 | Supply air controller: Alarm stop
0502 | A | 3 | N/A |  | X | Supply air controller: Rotor blocked | 5502 | Supply air controller: Rotor blocked
0503 | B | 3 | N/A | X |  | Supply air controller: Power restriction active | 5503 | Supply air controller: Power restriction active
0504 | B | 3 | N/A | X |  | Supply air controller: Low supply voltage (Vlo) | 5504 | Supply air controller: Low supply voltage (Vlo)
0505 | B | 3 | N/A | X |  | Supply air controller: High supply voltage (Vhi) | 5505 | Supply air controller: High supply voltage (Vhi)
0506 | B | 3 | N/A | X |  | Supply air controller: High temperature (Thi) | 5506 | Supply air controller: High temperature (Thi)
0507 | B | 3 | N/A | X |  | Supply air controller: High internal ripple voltage | 5507 | Supply air controller: High internal ripple voltage
0508 | B | 3 | N/A | X |  | Supply air controller: Loss of supply phase | 5508 | Supply air controller: Loss of supply phase
0509 | A | 3 | N/A |  | X | Supply air controller: EEPROM error | 5509 | Supply air controller: EEPROM error
0510 | A | 3 | N/A |  | X | Supply air fan: Alarminput active | 5510 | Supply air fan: Alarminput active
0511 | A | 3 | N/A | X | X | Supply air: Flowregulation not possible, no Pressure transmitter mounted | 5511 | Supply air: Flowregulation not possible, no Pressure transmitter mounted
0512 | B | 10 | N/A | X |  | Supply air: Pressure readings too low, check pressure sensor and fan | 5512 | Supply air: Pressure readings too low, check pressure sensor and fan
0601 | A | 3 | N/A |  | X | Exhaust air controller: Alarm stop | 5601 | Exhaust air controller: Alarm stop
0602 | A | 3 | N/A |  | X | Exhaust air controller: Rotor blocked | 5602 | Exhaust air controller: Rotor blocked
0603 | B | 3 | N/A | X |  | Exhaust air controller: Power restriction active | 5603 | Exhaust air controller: Power restriction active
0604 | B | 3 | N/A | X |  | Exhaust air controller: Low supply voltage (Vlo) | 5604 | Exhaust air controller: Low supply voltage (Vlo)
0605 | B | 3 | N/A | X |  | Exhaust air controller: High supply voltage (Vhi) | 5605 | Exhaust air controller: High supply voltage (Vhi)
0606 | B | 3 | N/A | X |  | Exhaust air controller: High temperature (Thi) | 5606 | Exhaust air controller: High temperature (Thi)
0607 | B | 3 | N/A | X |  | Exhaust air controller: High internal ripple voltage | 5607 | Exhaust air controller: High internal ripple voltage
0608 | B | 3 | N/A | X |  | Exhaust air controller: Loss of supply phase | 5608 | Exhaust air controller: Loss of supply phase
0609 | A | 3 | N/A |  | X | Exhaust air controller: EEPROM error | 5609 | Exhaust air controller: EEPROM error
0610 | A | 3 | N/A |  | X | Exhaust air fan: Alarminput active | 5610 | Exhaust air fan: Alarminput active
0611 | A | 3 | N/A | X | X | Exhaust air: Flowregulation not possible, no Pressure transmitter mounted | 5611 | Exhaust air: Flowregulation not possible, no Pressure transmitter mounted
0612 | B | 10 | N/A | X |  | Exhaust air: Pressure readings too low, check pressure sensor and fan | 5612 | Exhaust air: Pressure readings too low, check pressure sensor and fan
Alarmlist, OJ-AHC-3000 SW 2.10 | [5 empty] | HMI alarm text |  | OJ-Air Cloud
Alarm Number | Priority | Alarm- delay sec. | Alarm Limit | Auto reset | Unit stop | Alarm text | Alarm Number | Alarm text
0701 | B | 1200 | N/A | X |  | Airflow compensation of outdoor air filter monitor is not measured | 5701 | Airflow compensation of outdoor air filter monitor is not measured
0702 | B | 10 | N/A |  |  | Pressure drop across outdoor air filter too high, filter blocked | 5702 | Pressure drop across outdoor air filter too high, filter blocked
0703 | B | 10 | N/A |  |  | Replace outdoor air filter and reset filter replacement timer | 5703 | Replace outdoor air filter and reset filter replacement timer
0704 | B | 10 | N/A |  |  | Outdoor air filter - pressure switch - active | 5704 | Outdoor air filter - pressure switch - active
0708 | B | 10 | N/A |  |  | Supply air filter - pressure switch - active | 5708 | Supply air filter - pressure switch - active
0709 | B | 1200 | N/A | X |  | Airflow compensation of extract air filter monitor is not measured | 5709 | Airflow compensation of extract air filter monitor is not measured
0710 | B | 10 | N/A |  |  | Pressure drop across extract air filter too high, filter blocked | 5710 | Pressure drop across extract air filter too high, filter blocked
0711 | B | 10 | N/A |  |  | Replace extract air filter and reset filter replacement timer | 5711 | Replace extract air filter and reset filter replacement timer
0712 | B | 10 | N/A |  |  | Extract air filter – pressure switch - active | 5712 | Extract air filter – pressure switch - active
0713 | B | 10 | N/A | X |  | Airflow compensation filter monitor interrupted, no stable signal. | 5713 | Airflow compensation filter monitor interrupted, no stable signal.
0801 | A | 10 | N/A | X | X | Supply air fan, alarm | 5801 | Supply air fan, alarm
0802 | B | 600 | -10% | X |  | Low supply airflow | 5802 | Low supply airflow
0803 | B | 600 | +10% | X |  | High supply airflow | 5803 | High supply airflow
0804 | B | 600 | -10% | X |  | Low supply air pressure | 5804 | Low supply air pressure
0805 | A | 600 | +10% |  | X | High supply air pressure | 5805 | High supply air pressure
0901 | A | 10 | N/A | X | X | Exhaust air fan, alarm | 5901 | Exhaust air fan, alarm
0902 | B | 600 | -10% | X |  | Low extract airflow | 5902 | Low extract airflow
0903 | B | 600 | +10% | X |  | High extract airflow | 5903 | High extract airflow
0904 | B | 600 | -10% | X |  | Low extract air pressure | 5904 | Low extract air pressure
0905 | A | 600 | +10% |  | X | High extract air pressure | 5905 | High extract air pressure
1001 | A | 600 | -5°C |  | X | Low supply air temperature | 6001 | Low supply air temperature
1002 | B | 600 | +5°C | X |  | High supply air temperature | 6002 | High supply air temperature
1003 | B | 1200 | -5°C | X |  | Low extract air temperature | 6003 | Low extract air temperature
1004 | B | 1200 | +5°C | X |  | High extract air temperature | 6004 | High extract air temperature
1101 | B | 300 | N/A | X |  | Rotary heat exchanger: No rotation | 6101 | Rotary heat exchanger: No rotation
1102 | B | 300 | N/A | X |  | Rotary heat exchanger: Low supply voltage (Vlo) | 6102 | Rotary heat exchanger: Low supply voltage (Vlo)
1103 | B | 300 | N/A | X |  | Rotary heat exchanger: High supply voltage (Vhi) | 6103 | Rotary heat exchanger: High supply voltage (Vhi)
1104 | B | 300 | N/A | X |  | Rotary heat exchanger: High output current (Ihi) | 6104 | Rotary heat exchanger: High output current (Ihi)
1105 | B | 300 | N/A | X |  | Rotary heat exchanger: High internal temperature | 6105 | Rotary heat exchanger: High internal temperature
1106 | B | 300 | N/A | X |  | Rotary heat exchanger: Torque overload | 6106 | Rotary heat exchanger: Torque overload
1201 | B | 3 | N/A | X |  | Dynamic de-icing crossflow heatexchanger not measured | 6201 | Dynamic de-icing crossflow heatexchanger not measured
1202 | B | 3 | N/A | X |  | Pressure drop over exchanger to high, exchanger frozen | 6202 | Pressure drop over exchanger to high, exchanger frozen
1203 | B | 3 | N/A | X |  | Airflow compensation measurement interrupted, no stable signal | 6203 | Airflow compensation measurement interrupted, no stable signal
1301 | A | 10 | N/A |  | X | Pump alarm: Water heating coil 1 | 6301 | Pump alarm: Water heating coil 1
1401 | B | 300 | N/A | X |  | Heating 1 cut out due to low airflow | 6401 | Heating 1 cut out due to low airflow
1402 | B | 3 | N/A |  |  | Electric heating coil 1: overheating alarm | 6402 | Electric heating coil 1: overheating alarm
1501 | B | 10 | N/A | X |  | Satellite 1 : No communication | 6501 | Satellite 1 : No communication
1502 | B | 10 | N/A | X |  | Satellite 2 : No communication | 6502 | Satellite 2 : No communication
1503 | B | 10 | N/A | X |  | Satellite 3 : No communication | 6503 | Satellite 3 : No communication
1504 | B | 10 | N/A | X |  | Satellite 4 : No communication | 6504 | Satellite 4 : No communication
1505 | B | 10 | N/A | X |  | Satellite 5 : No communication | 6505 | Satellite 5 : No communication
1506 | B | 10 | N/A | X |  | Satellite 6 : No communication | 6506 | Satellite 6 : No communication
1507 | B | 10 | N/A | X |  | Satellite 7 : No communication | 6507 | Satellite 7 : No communication
1508 | B | 10 | N/A | X |  | Satellite 8 : No communication | 6508 | Satellite 8 : No communication
1509 | B | 10 | N/A | X |  | Satellite 9 : No communication | 6509 | Satellite 9 : No communication
1510 | B | 10 | N/A | X |  | Satellite 10 : No communication | 6510 | Satellite 10 : No communication
1511 | B | 10 | N/A | X |  | Satellite 11 : No communication | 6511 | Satellite 11 : No communication
1512 | B | 10 | N/A | X |  | Satellite 12 : No communication | 6512 | Satellite 12 : No communication
1513 | B | 10 | N/A | X |  | Satellite 13 : No communication | 6513 | Satellite 13 : No communication
1514 | B | 10 | N/A | X |  | Satellite 14 : No communication | 6514 | Satellite 14 : No communication
Alarmlist, OJ-AHC-3000 SW 2.10 | [5 empty] | HMI alarm text |  | OJ-Air Cloud
Alarm Number | Priority | Alarm- delay sec. | Alarm Limit | Auto reset | Unit stop | Alarm text | Alarm Number | Alarm text
1601 | A | 3 | N/A |  | X | Frost alarm: Water heating coil 1 | 6601 | Frost alarm: Water heating coil 1
1602 | A | 3 | N/A |  | X | Combi-coil heating frost alarm | 6602 | Combi-coil heating frost alarm
1603 | A | 3 | N/A |  | X | Water heating coil 1 Frost alarm: Digital input | 6603 | Water heating coil 1 Frost alarm: Digital input
1604 | A | 3 | N/A |  | X | Combi-coil Frost alarm: Digital input | 6604 | Combi-coil Frost alarm: Digital input
1608 | A | 3 | N/A | X | X | Heating coil: No frostguard, activate Temperature-Sensor and/or Capillartube input. | 6608 | Heating coil: No frostguard, activate Temperature-Sensor and/or Capillartube input.
1701 | A | 10 | N/A | X | X | Temperature sensor error: Supply air | 6701 | Temperature sensor error: Supply air
1702 | A | 10 | N/A | X | X | Temperature sensor error: Extract air | 6702 | Temperature sensor error: Extract air
1703 | A | 10 | N/A | X | X | Temperature sensor error: Room | 6703 | Temperature sensor error: Room
1704 | A | 10 | N/A | X | X | Temperature sensor error: Exhaust air | 6704 | Temperature sensor error: Exhaust air
1705 | A | 10 | N/A | X | X | Temperature sensor error: Outdoor air temperature (Internal) | 6705 | Temperature sensor error: Outdoor air temperature (Internal)
1706 | B | 10 | N/A | X |  | Temperature sensor error: Outdoor air temperature (External) | 6706 | Temperature sensor error: Outdoor air temperature (External)
1707 | A | 10 | N/A | X | X | Temperature sensor error: Water heating coil 1 | 6707 | Temperature sensor error: Water heating coil 1
1708 | A | 10 | N/A | X | X | Temperature sensor error: Heat recovery | 6708 | Temperature sensor error: Heat recovery
1801 | B | 10 | N/A | X |  | Satellite 1 : Alarm triggered | 6801 | Satellite 1 : Alarm triggered
1802 | B | 10 | N/A | X |  | Satellite 2 : Alarm triggered | 6802 | Satellite 2 : Alarm triggered
1803 | B | 10 | N/A | X |  | Satellite 3 : Alarm triggered | 6803 | Satellite 3 : Alarm triggered
1804 | B | 10 | N/A | X |  | Satellite 4 : Alarm triggered | 6804 | Satellite 4 : Alarm triggered
1805 | B | 10 | N/A | X |  | Satellite 5 : Alarm triggered | 6805 | Satellite 5 : Alarm triggered
1806 | B | 10 | N/A | X |  | Satellite 6 : Alarm triggered | 6806 | Satellite 6 : Alarm triggered
1807 | B | 10 | N/A | X |  | Satellite 7 : Alarm triggered | 6807 | Satellite 7 : Alarm triggered
1808 | B | 10 | N/A | X |  | Satellite 8 : Alarm triggered | 6808 | Satellite 8 : Alarm triggered
1809 | B | 10 | N/A | X |  | Satellite 9 : Alarm triggered | 6809 | Satellite 9 : Alarm triggered
1810 | B | 10 | N/A | X |  | Satellite 10 : Alarm triggered | 6810 | Satellite 10 : Alarm triggered
1811 | B | 10 | N/A | X |  | Satellite 11 : Alarm triggered | 6811 | Satellite 11 : Alarm triggered
1812 | B | 10 | N/A | X |  | Satellite 12 : Alarm triggered | 6812 | Satellite 12 : Alarm triggered
1813 | B | 10 | N/A | X |  | Satellite 13 : Alarm triggered | 6813 | Satellite 13 : Alarm triggered
1814 | B | 10 | N/A | X |  | Satellite 14 : Alarm triggered | 6814 | Satellite 14 : Alarm triggered
1901 | B | 10 | N/A |  |  | Cooling error: Alarm from cooling appliance. | 6901 | Cooling error: Alarm from cooling appliance.
2001 | A | 10 | N/A | X | X | Temperature sensor error: combi-coil | 7001 | Temperature sensor error: combi-coil
2002 | A | 10 | N/A |  | X | Pump alarm combi-coil | 7002 | Pump alarm combi-coil
2205 | B | 1200 | N/A | X |  | High air humidity in the extract air | 7205 | High air humidity in the extract air
2206 | B | 1200 | N/A | X |  | Low air humidity in the extract air | 7206 | Low air humidity in the extract air
2207 | B | 10 | N/A | X |  | Humidity sensor error. Sensor disconnectet/short-circuited | 7207 | Humidity sensor error. Sensor disconnectet/short-circuited
2301 | B | 1200 | N/A | X |  | CO2 level is too high | 7301 | CO2 level is too high
2302 | B | 3 | N/A | X |  | CO2 sensor not configured | 7302 | CO2 sensor not configured
2303 | B | 10 | N/A | X |  | CO2 sensor error: Sensor disconnected/short-circuited | 7303 | CO2 sensor error: Sensor disconnected/short-circuited
2401 | B | 1200 | N/A | X |  | VOC level is too high | 7401 | VOC level is too high
2403 | B | 10 | N/A | X |  | VOC sensor (VTH-6202): No communication | 7403 | VOC sensor (VTH-6202): No communication
2404 | B | 600 | N/A | X |  | VTH-6202, VOC sensor error | 7404 | VTH-6202, VOC sensor error
Alarmlist, OJ-AHC-3000 SW 2.10 | [5 empty] | HMI alarm text |  | OJ-Air Cloud
Alarm Number | Priority | Alarm- delay sec. | Alarm Limit | Auto reset | Unit stop | Alarm text | Alarm Number | Alarm text
2406 | B | 10 | N/A | X |  | Communication Error Room-Master 2 | 7406 | Communication Error Room-Master 2
2407 | B | 10 | N/A | X |  | Communication Error Room-Master 3 | 7407 | Communication Error Room-Master 3
2408 | B | 10 | N/A | X |  | Communication Error Room-Master 4 | 7408 | Communication Error Room-Master 4
2409 | B | 10 | N/A | X |  | Communication Error Room-Master 5 | 7409 | Communication Error Room-Master 5
2410 | B | 10 | N/A | X |  | Communication Error Room-Master 6 | 7410 | Communication Error Room-Master 6
2411 | B | 10 | N/A | X |  | Communication Error Room-Master 7 | 7411 | Communication Error Room-Master 7
2412 | B | 10 | N/A | X |  | Communication Error Room-Master 8 | 7412 | Communication Error Room-Master 8
2413 | B | 10 | N/A | X |  | Communication Error Room-Master 9 | 7413 | Communication Error Room-Master 9
2414 | B | 10 | N/A | X |  | Communication Error Room-Master 10 | 7414 | Communication Error Room-Master 10
2415 | B | 10 | N/A | X |  | Communication Error Room-Master 11 | 7415 | Communication Error Room-Master 11
2501 | B | 10 | N/A | X |  | Communication Error Room-Master 12 | 7501 | Communication Error Room-Master 12
2502 | B | 10 | N/A | X |  | Communication Error Room-Master 13 | 7502 | Communication Error Room-Master 13
2503 | B | 10 | N/A | X |  | Communication Error Room-Master 14 | 7503 | Communication Error Room-Master 14
2504 | B | 10 | N/A | X |  | Communication Error Room-Master 15 | 7504 | Communication Error Room-Master 15
2505 | B | 10 | N/A | X |  | Communication Error Room-Master 16 | 7505 | Communication Error Room-Master 16
2506 | B | 10 | N/A | X |  | Communication Error Room-Master 17 | 7506 | Communication Error Room-Master 17
2507 | B | 10 | N/A | X |  | Communication Error Room-Master 18 | 7507 | Communication Error Room-Master 18
2508 | B | 10 | N/A | X |  | Communication Error Room-Master 19 | 7508 | Communication Error Room-Master 19
2509 | B | 10 | N/A | X |  | Communication Error Room-Master 20 | 7509 | Communication Error Room-Master 20
2510 | B | 10 | N/A | X |  | Communication Error Room-Master 21 | 7510 | Communication Error Room-Master 21
2511 | B | 10 | N/A | X |  | Communication Error Room-Master 22 | 7511 | Communication Error Room-Master 22
2512 | B | 10 | N/A | X |  | Communication Error Room-Master 23 | 7512 | Communication Error Room-Master 23
2513 | B | 10 | N/A | X |  | Communication Error Room-Master 24 | 7513 | Communication Error Room-Master 24
2514 | B | 10 | N/A | X |  | Communication Error Room-Master 25 | 7514 | Communication Error Room-Master 25